## Verzeichnis
Bibliothek 2 | AMEV-Profile, Objekt-Templates
Tabellen-Nr. | Tabellen-Bezeichnung
Tabelle 6 | AMEV-Profil AS-C und AS-D (Prüftabelle)
Tabelle 8.1 | AI-Templates
Tabelle 8.2 | AO- und AV-Templates
Tabelle 8.3 | BI-Templates
Tabelle 8.4 | BO- und BV-Templates
Tabelle 8.5 | CAL-Templates
Tabelle 8.6 | DEV-Templates
Tabelle 8.7 | EE-Templates
Tabelle 8.8 | LP-Templates
Tabelle 8.9 | MI-Templates
Tabelle 8.10 | MO- und MV-Templates
Tabelle 8.11 | NC-Templates
Tabelle 8.12 | SCH-Templates
Tabelle 8.13 | SV-Templates
Tabelle 8.14 | TL-Templates
Tabelle 15 | Funktionsbereich
Tabelle 16 | Zuständigkeitskennung
Tabelle 17 | Zuständigkeitstabelle
Tabelle 23 | Minimum Character_String_Length
Tabelle 24 | Priority_Array
Tabelle 25 | Meldeklasse
Tabelle 26 | EventParameter

## Änderungen
Version | Datum | Arbeitsblatt | Kurzbeschreibung der Änderung | Short description of the change (draft)
AMEV1.1 | 2025-02-14 | 6 AMEV-Profil AS-C + AS-D | Spalte A: blaue Markierung, wenn in Datenzeile Änderungen erfolgen Spalte H & L: Fußnote eingefügt Spalte L: Anpassung "List_Of_Object_Property_References" -> "List_Of_Object_Property_Reference" | Column A: Blue marking if changes are made in data row Column H & L: Footnote inserted Column L: Customization "List_Of_Object_Property_References" -> "List_Of_Object_Property_Reference"
|  | 8.1 AI bis 8.14 TL | Spalte A: Blaue Markierung, wenn in Datenzeile Änderungen erfolgen Spalte eingefügt für Description Spalte eingefügt zur Kennzeichnung "Letztmalige Änderung in Version" | Column A: Blue marking if changes are made in data row Column inserted for description Column inserted to indicate "Last change in version"
|  | 8.1 AI | Im englischen Teil "fix" durch "specify" ersetzt - ohne Markerung | In the english part "fix" replaced by "specify" - without marking
|  | 8.2 AO_AV | Spalte C: Zwei Templates umbenannt, an vorhandene Templates angepasst Im englischen Teil "fix" durch "specify" ersetzt - ohne Markierung | Column C: Two templates renamed, adapted to existing templates In the english part "fix" replaced by "specify" - without marking
|  | 8.3 BI | Spalte A - C: Drei Templates eingefügt | Column A - C: Three templates inserted
|  | 8.4 BO_BV | Änderung hochgestellte Eins in ASCII Zeichen ¹ (0185) - ohne Markierung | Change superscript one to ASCII character ¹ (0185) - without marker
|  | 8.6 DEV | Spalte U & V: Fußnote eingefügt | Column U & V: Footnote inserted
|  | 8.7 EE | Spalte J: Eintrag korrigiert | Column J: Entry corrected
|  | 8.9 MI | Übersetzung angepasst | Translation adapted
|  | 8.10 MO_MV | Änderung hochgestellte Eins in ASCII Zeichen ¹ (0185) - ohne Markierung | Change superscript one to ASCII character ¹ (0185) - without marker
|  | 17 Zuständigkeitstabelle | Änderungen in Spalte Q, U und V | Changes in Column Q, U and V
|  | 23 MinCharStringLength | Spalten C & D: State_Text mit Klarstellung | Columns C & D: State_Text with clarification
AMEV1 | 2024-04-12

## 6 AMEV-Profil AS-C + AS-D
Zeile | PROP NR | OBJ | [5 empty] | AMEV-Profile AS-C und AS-D
0 | [7 empty] | (Prüftabelle)
1
2 | [5 empty] | 1. Allgemeine Angaben
3 | [5 empty] | Anbieter
4 | [5 empty] | Vendor ID
5 | [5 empty] | Typ Nummer
6 | [5 empty] | Firmware-Revision
7 | [5 empty] | Prüf-Bericht
8
9 | [5 empty] | Profil AS-C |  |  | Profil AS-D
10
11 | [5 empty] | 2. BIBBs |  |  | 2. BIBBs
12 | [5 empty] | BIBBs | Vorgabe | geprüft | BIBBs | Vorgabe | geprüft
13 | 0 |  |  |  |  | 1 | 2 | 3 | 1 | 2 | 3
14 | 1 |  |  |  |  | DS-RP-A | X |  | DS-RP-A | X
15 | 2 |  |  |  |  | DS-RP-B | X |  | DS-RP-B | X
16 | 3 |  |  |  |  | DS-RPM-A | X |  | DS-RPM-A | X
17 | 4 |  |  |  |  | DS-RPM-B | X |  | DS-RPM-B | X
18 | 5 |  |  |  |  | DS-WP-A | X |  | DS-WP-A | X
19 | 6 |  |  |  |  | DS-WP-B | X |  | DS-WP-B | X
20 | 7 |  |  |  |  | DS-WPM-B | X |  | DS-WPM-B | X
21 | 8 |  |  |  |  | DS-COV-A | X |  | DS-COV-A | X
22 | 9 |  |  |  |  | DS-COV-B | X |  | DS-COV-B | X
23 | 10 |  |  |  |  | AE-N-I-B | X |  | AE-N-I-B | X
24 | 11 |  |  |  |  | AE-ACK-B | X |  | AE-ACK-B | X
25 | 12 |  |  |  |  | AE-ESUM-B | X |  | AE-ESUM-B | X
26 | 13 |  |  |  |  | AE-INFO-B | X |  | AE-INFO-B | X
27 | 14 |  |  |  |  | SCHED-I-B | X |  | SCHED-I-B | X
28 | 15 |  |  |  |  | DM-DDB-A | X |  | DM-DDB-A | X
29 | 16 |  |  |  |  | DM-DDB-B | X |  | DM-DDB-B | X
30 | 17 |  |  |  |  | DM-DOB-B | X |  | DM-DOB-B | X
31 | 18 |  |  |  |  | DM-DCC-B | X |  | DM-DCC-B | X
32 | 19 |  |  |  |  | DM-TS-B | XT |  | DM-TS-B | XT
33 | 20 |  |  |  |  | DM-UTC-B | XT |  | DM-UTC-B | XT
34 | 21 |  |  |  |  | DM-RD-B | X |  | DM-RD-B | X
35 | 22 |  |  |  |  | DM-BR-B | X |  | DM-BR-B | X
36 | 23 |  |  |  |  | DS-COVP-B | X |  | DS-COVP-B | X
37 | 24 |  |  |  |  | AE-N-E-B | X |  | AE-N-E-B | X
38 | 25 |  |  |  |  | AE-ASUM-B | X |  | AE-ASUM-B | X
39 | 26 |  |  |  |  | SCHED-E-B | X |  | SCHED-E-B | X
40 | 27 |  |  |  |  | T-VMT-I-B | X |  | T-VMT-I-B | X
41 | 28 |  |  |  |  | T-VMT-E-B | X |  | T-VMT-E-B | X
42 | 29 |  |  |  |  | T-ATR-B | X |  | T-ATR-B | X
43 | 30 |  |  |  |  | DM-OCD-B | X |  | DM-OCD-B | X
44
45
46 | [5 empty] | 3. Objekttypen und DC/DD-Fähigkeiten |  |  | 3. Objekttypen und DC/DD-Fähigkeiten
47 | [5 empty] | Objekttyp | Vorgabe | geprüft | Objekttyp | Vorgabe | geprüft
48 | 0 |  |  |  |  | 1 | 2 | 3 | 1 | 2 | 3
49 | 1 |  |  |  |  | AI | X |  | AI | X
50 | 2 |  |  |  |  | AO | X |  | AO | X
51 | 3 |  |  |  |  | AV | X |  | AV | X
52 | 4 |  |  |  |  | BI | X |  | BI | X
53 | 5 |  |  |  |  | BO | X |  | BO | X
54 | 6 |  |  |  |  | BV | X |  | BV | X
55 | 7 |  |  |  |  | CAL (mit DC/DD) | X |  | CAL (mit DC/DD) | X
56 | 8 |  |  |  |  | DEV | X |  | DEV | X
57 | 9 |  |  |  |  | EE (mit DC/DD) | X |  | EE (mit DC/DD) | X
58 | 10 |  |  |  |  | FIL | X |  | FIL | X
59 | 11 |  |  |  |  | LP | X |  | LP | X
60 | 12 |  |  |  |  | MI * | X |  | MI * | X
61 | 13 |  |  |  |  | MO * | X |  | MO * | X
62 | 14 |  |  |  |  | MV | X |  | MV | X
63 | 15 |  |  |  |  | NC (mit DC/DD) | X |  | NC (mit DC/DD) | X
64 | 16 |  |  |  |  | SCH (mit DD(DC) | X |  | SCH (mit DD(DC) | X
65 | 17 | [7 empty] | SV | X
66 | 18 |  |  |  |  | TL (mit DC/DD) | X |  | TL (mit DC/DD) | X
67
68
69 | [5 empty] | 4. Objekttypen, Properties, Conformance Codes |  |  | 4. Objekttypen, Properties, Conformance Codes
70 |  |  | Objekttyp, Property | Zuständ | PropSort | Objekttyp, Property | Vorgabe | geprüft | Objekttyp, Property | Vorgabe | geprüft
71 |  |  | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
72 | 0 | AI | Analog Input |  |  | Analog Input |  |  | Analog Input
73 | 1 | AI | Object_Identifier | U | a71 | Object_Identifier | R |  | Object_Identifier | R
74 | 2 | AI | Object_Name | B | a11 | Object_Name | R |  | Object_Name | R
75 | 3 | AI | Object_Type | B | a13 | Object_Type | R |  | Object_Type | R
76 | 4 | AI |  |  |  | Present_Value | W1 |  | Present_Value | W1
77 | 5 | AI | Description | B | a12 | Description | W |  | Description | W
78 | 6 | AI |  |  |  | Device_Type | R |  | Device_Type | R
79 | 7 | AI |  |  |  | Status_Flags | R |  | Status_Flags | R
80 | 8 | AI |  |  |  | Event_State | R |  | Event_State | R
81 | 9 | AI |  |  |  | Reliability | W1 |  | Reliability | W1
82 | 10 | AI |  |  |  | Out_Of_Service | W |  | Out_Of_Service | W
83 | 11 | AI |  |  |  | Update_Interval | R |  | Update_Interval | R
84 | 12 | AI | Units | B | b11 | Units | W |  | Units | W
85 | 13 | AI | Min_Pres_Value | P | c45 | Min_Pres_Value | R |  | Min_Pres_Value | R
86 | 14 | AI | Max_Pres_Value | P | c46 | Max_Pres_Value | R |  | Max_Pres_Value | R
87 | 15 | AI | Resolution | P | b41 | Resolution | R |  | Resolution | R
88 | 16 | AI | COV_Increment | B | b17 | COV_Increment | W |  | COV_Increment | W
89 | 17 | AI | Time_Delay | P | c43 | Time_Delay | W |  | Time_Delay | W
90 | 18 | AI | Notification_Class | B | c11 | Notification_Class | W |  | Notification_Class | W
91 | 19 | AI | High_Limit | P | c48 | High_Limit | W |  | High_Limit | W
92 | 20 | AI | Low_Limit | P | c47 | Low_Limit | W |  | Low_Limit | W
93 | 21 | AI | Deadband | P | c50 | Deadband | W |  | Deadband | W
94 | 22 | AI | Limit_Enable | P | c49 | Limit_Enable | W |  | Limit_Enable | W
95 | 23 | AI | Event_Enable | B | c12 | Event_Enable | W |  | Event_Enable | W
96 | 24 | AI |  |  |  | Acked_Transitions | R |  | Acked_Transitions | R
97 | 25 | AI | Notify_Type | B | c13 | Notify_Type | W |  | Notify_Type | W
98 | 26 | AI |  |  |  | Event_Time_Stamps | R |  | Event_Time_Stamps | R
99 | 27 | AI |  |  |  | Event_Message_Texts | R |  | Event_Message_Texts | R
100 | 28 | AI | Event_Message_Texts_Config | B | c14 | Event_Message_Texts_Conf | W |  | Event_Message_Texts_Config | W
101 | 29 | AI | Event_Detection_Enable | B | c15 | Event_Detection_Enable | W |  | Event_Detection_Enable | W
102 | 30 | AI | Event_Algorithm_Inhibit_Ref | P | c42 | Event_Algorithm_Inhibit_Ref | RA |  | Event_Algorithm_Inhibit_Ref | RA
103 | 31 | AI | Event_Algorithm_Inhibit | P | c41 | Event_Algorithm_Inhibit | RA |  | Event_Algorithm_Inhibit | RA
104 | 32 | AI | Time_Delay_Normal | P | c44 | Time_Delay_Normal | W |  | Time_Delay_Normal | W
105 | 33 | AI |  |  |  | Reliability_Evaluation_Inhibit | RX¦O |  | Reliability_Evaluation_Inhibit | RX¦O
106 | 34 | AI |  |  |  | Property_List | R |  | Property_List | R
107
108 |  |  | Objekttyp, Property | Zuständ | PropSort | Objekttyp, Property | Vorgabe | geprüft | Objekttyp, Property | Vorgabe | geprüft
109 |  |  | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
110 | 0 | AO | Analog Output |  |  | Analog Output |  |  | Analog Output
111 | 1 | AO | Object_Identifier | U | a71 | Object_Identifier | R |  | Object_Identifier | R
112 | 2 | AO | Object_Name | B | a11 | Object_Name | R |  | Object_Name | R
113 | 3 | AO | Object_Type | B | a13 | Object_Type | R |  | Object_Type | R
114 | 4 | AO |  |  |  | Present_Value | W1 |  | Present_Value | W1
115 | 5 | AO | Description | B | a12 | Description | W |  | Description | W
116 | 6 | AO |  |  |  | Device_Type | R |  | Device_Type | R
117 | 7 | AO |  |  |  | Status_Flags | R |  | Status_Flags | R
118 | 8 | AO |  |  |  | Event_State | R |  | Event_State | R
119 | 9 | AO |  |  |  | Reliability | W1 |  | Reliability | W1
120 | 10 | AO |  |  |  | Out_Of_Service | W |  | Out_Of_Service | W
121 | 11 | AO | Units | B | b11 | Units | W |  | Units | W
122 | 12 | AO | Min_Pres_Value | P | c45 | Min_Pres_Value | R |  | Min_Pres_Value | R
123 | 13 | AO | Max_Pres_Value | P | c46 | Max_Pres_Value | R |  | Max_Pres_Value | R
124 | 14 | AO | Resolution | P | b41 | Resolution | R |  | Resolution | R
125 | 15 | AO |  |  |  | Priority_Array | R |  | Priority_Array | R
126 | 16 | AO | Relinquish_Default | B | b16 | Relinquish_Default | W |  | Relinquish_Default | W
127 | 17 | AO | COV_Increment | B | b17 | COV_Increment | W |  | COV_Increment | W
128 | 18 | AO | Time_Delay | P | c43 | Time_Delay | W |  | Time_Delay | W
129 | 19 | AO | Notification_Class | B | c11 | Notification_Class | W |  | Notification_Class | W
130 | 20 | AO | High_Limit | P | c48 | High_Limit | W |  | High_Limit | W
131 | 21 | AO | Low_Limit | P | c47 | Low_Limit | W |  | Low_Limit | W
132 | 22 | AO | Deadband | P | c50 | Deadband | W |  | Deadband | W
133 | 23 | AO | Limit_Enable | P | c49 | Limit_Enable | W |  | Limit_Enable | W
134 | 24 | AO | Event_Enable | B | c12 | Event_Enable | W |  | Event_Enable | W
135 | 25 | AO |  |  |  | Acked_Transitions | R |  | Acked_Transitions | R
136 | 26 | AO | Notify_Type | B | c13 | Notify_Type | W |  | Notify_Type | W
137 | 27 | AO |  |  |  | Event_Time_Stamps | R |  | Event_Time_Stamps | R
138 | 28 | AO |  |  |  | Event_Message_Texts | R |  | Event_Message_Texts | R
139 | 29 | AO | Event_Message_Texts_Config | B | c14 | Event_Message_Texts_Conf | W |  | Event_Message_Texts_Config | W
140 | 30 | AO | Event_Detection_Enable | B | c15 | Event_Detection_Enable | W |  | Event_Detection_Enable | W
141 | 31 | AO | Event_Algorithm_Inhibit_Ref | P | c42 | Event_Algorithm_Inhibit_Ref | RA |  | Event_Algorithm_Inhibit_Ref | RA
142 | 32 | AO | Event_Algorithm_Inhibit | P | c41 | Event_Algorithm_Inhibit | RA |  | Event_Algorithm_Inhibit | RA
143 | 33 | AO | Time_Delay_Normal | P | c44 | Time_Delay_Normal | W |  | Time_Delay_Normal | W
144 | 34 | AO |  |  |  | Reliability_Evaluation_Inhibit | RX¦O |  | Reliability_Evaluation_Inhibit | RX¦O
145 | 35 | AO |  |  |  | Property_List | R |  | Property_List | R
146 | 36 | AO |  |  |  | Current_Command_Priority | R22 |  | Current_Command_Priority | R22
147
148 |  |  | Objekttyp, Property | Zuständ | PropSort | Objekttyp, Property | Vorgabe | geprüft | Objekttyp, Property | Vorgabe | geprüft
149 |  |  | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
150 | 0 | AV | Analog Value |  |  | Analog Value |  |  | Analog Value
151 | 1 | AV | Object_Identifier | U | a71 | Object_Identifier | R |  | Object_Identifier | R
152 | 2 | AV | Object_Name | B | a11 | Object_Name | R |  | Object_Name | R
153 | 3 | AV | Object_Type | B | a13 | Object_Type | R |  | Object_Type | R
154 | 4 | AV |  |  |  | Present_Value | W1 |  | Present_Value | W1
155 | 5 | AV | Description | B | a12 | Description | W |  | Description | W
156 | 6 | AV |  |  |  | Status_Flags | R |  | Status_Flags | R
157 | 7 | AV |  |  |  | Event_State | R |  | Event_State | R
158 | 8 | AV |  |  |  | Reliability | W1 |  | Reliability | W1
159 | 9 | AV |  |  |  | Out_Of_Service | W |  | Out_Of_Service | W
160 | 10 | AV | Units | B | b11 | Units | W |  | Units | W
161 | 11 | AV | Min_Pres_Value | P | c45 | Min_Pres_Value | R |  | Min_Pres_Value | R
162 | 12 | AV | Max_Pres_Value | P | c46 | Max_Pres_Value | R |  | Max_Pres_Value | R
163 | 13 | AV |  |  |  | Priority_Array | R |  | Priority_Array | R
164 | 14 | AV | Relinquish_Default | B | b16 | Relinquish_Default | W |  | Relinquish_Default | W
165 | 15 | AV | COV_Increment | B | b17 | COV_Increment | W |  | COV_Increment | W
166 | 16 | AV | Time_Delay | P | c43 | Time_Delay | W |  | Time_Delay | W
167 | 17 | AV | Notification_Class | B | c11 | Notification_Class | W |  | Notification_Class | W
168 | 18 | AV | High_Limit | P | c48 | High_Limit | W |  | High_Limit | W
169 | 19 | AV | Low_Limit | P | c47 | Low_Limit | W |  | Low_Limit | W
170 | 20 | AV | Deadband | P | c50 | Deadband | W |  | Deadband | W
171 | 21 | AV | Limit_Enable | P | c49 | Limit_Enable | W |  | Limit_Enable | W
172 | 22 | AV | Event_Enable | B | c12 | Event_Enable | W |  | Event_Enable | W
173 | 23 | AV |  |  |  | Acked_Transitions | R |  | Acked_Transitions | R
174 | 24 | AV | Notify_Type | B | c13 | Notify_Type | W |  | Notify_Type | W
175 | 25 | AV |  |  |  | Event_Time_Stamps | R |  | Event_Time_Stamps | R
176 | 26 | AV |  |  |  | Event_Message_Texts | R |  | Event_Message_Texts | R
177 | 27 | AV | Event_Message_Texts_Config | B | c14 | Event_Message_Texts_Conf | W |  | Event_Message_Texts_Config | W
178 | 28 | AV | Event_Detection_Enable | B | c15 | Event_Detection_Enable | W |  | Event_Detection_Enable | W
179 | 29 | AV | Event_Algorithm_Inhibit_Ref | P | c42 | Event_Algorithm_Inhibit_Ref | RA |  | Event_Algorithm_Inhibit_Ref | RA
180 | 30 | AV | Event_Algorithm_Inhibit | P | c41 | Event_Algorithm_Inhibit | RA |  | Event_Algorithm_Inhibit | RA
181 | 31 | AV | Time_Delay_Normal | P | c44 | Time_Delay_Normal | W |  | Time_Delay_Normal | W
182 | 32 | AV |  |  |  | Reliability_Evaluation_Inhibit | RX¦O |  | Reliability_Evaluation_Inhibit | RX¦O
183 | 33 | AV |  |  |  | Property_List | R |  | Property_List | R
184 | 34 | AV |  |  |  | Current_Command_Priority | R22 |  | Current_Command_Priority | R22
185
186 |  |  | Objekttyp, Property | Zuständ | PropSort | Objekttyp, Property | Vorgabe | geprüft | Objekttyp, Property | Vorgabe | geprüft
187 |  |  | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
188 | 0 | BI | Binary Input |  |  | Binary Input |  |  | Binary Input
189 | 1 | BI | Object_Identifier | U | a71 | Object_Identifier | R |  | Object_Identifier | R
190 | 2 | BI | Object_Name | B | a11 | Object_Name | R |  | Object_Name | R
191 | 3 | BI | Object_Type | B | a13 | Object_Type | R |  | Object_Type | R
192 | 4 | BI |  |  |  | Present_Value | W1 |  | Present_Value | W1
193 | 5 | BI | Description | B | a12 | Description | W |  | Description | W
194 | 6 | BI |  |  |  | Device_Type | R |  | Device_Type | R
195 | 7 | BI |  |  |  | Status_Flags | R |  | Status_Flags | R
196 | 8 | BI |  |  |  | Event_State | R |  | Event_State | R
197 | 9 | BI |  |  |  | Reliability | W1 |  | Reliability | W1
198 | 10 | BI |  |  |  | Out_Of_Service | W |  | Out_Of_Service | W
199 | 11 | BI | Polarity | B | b12 | Polarity | W |  | Polarity | W
200 | 12 | BI | Inactive_Text | B | b13 | Inactive_Text | R |  | Inactive_Text | R
201 | 13 | BI | Active_Text | B | b14 | Active_Text | R |  | Active_Text | R
202 | 14 | BI |  |  |  | Change_Of_State_Time | R |  | Change_Of_State_Time | R
203 | 15 | BI |  |  |  | Change_Of_State_Count | R0 |  | Change_Of_State_Count | R0
204 | 16 | BI |  |  |  | Time_Of_State_Count_Reset | R |  | Time_Of_State_Count_Reset | R
205 | 17 | BI |  |  |  | Elapsed_Active_Time | R0 |  | Elapsed_Active_Time | RO
206 | 18 | BI |  |  |  | Time_Of_Active_Time_Reset | R |  | Time_Of_Active_Time_Reset | R
207 | 19 | BI | Time_Delay | P | c43 | Time_Delay | W |  | Time_Delay | W
208 | 20 | BI | Notification_Class | B | c11 | Notification_Class | W |  | Notification_Class | W
209 | 21 | BI | Alarm_Value | B | c16 | Alarm_Value | W |  | Alarm_Value | W
210 | 22 | BI | Event_Enable | B | c12 | Event_Enable | W |  | Event_Enable | W
211 | 23 | BI |  |  |  | Acked_Transitions | R |  | Acked_Transitions | R
212 | 24 | BI | Notify_Type | B | c13 | Notify_Type | W |  | Notify_Type | W
213 | 25 | BI |  |  |  | Event_Time_Stamps | R |  | Event_Time_Stamps | R
214 | 26 | BI |  |  |  | Event_Message_Texts | R |  | Event_Message_Texts | R
215 | 27 | BI | Event_Message_Texts_Config | B | c14 | Event_Message_Texts_Conf | W |  | Event_Message_Texts_Config | W
216 | 28 | BI | Event_Detection_Enable | B | c15 | Event_Detection_Enable | W |  | Event_Detection_Enable | W
217 | 29 | BI | Event_Algorithm_Inhibit_Ref | P | c42 | Event_Algorithm_Inhibit_Ref | RA |  | Event_Algorithm_Inhibit_Ref | RA
218 | 30 | BI | Event_Algorithm_Inhibit | P | c41 | Event_Algorithm_Inhibit | RA |  | Event_Algorithm_Inhibit | RA
219 | 31 | BI | Time_Delay_Normal | P | c44 | Time_Delay_Normal | W |  | Time_Delay_Normal | W
220 | 32 | BI |  |  |  | Reliability_Evaluation_Inhibit | RX¦O |  | Reliability_Evaluation_Inhibit | RX¦O
221 | 33 | BI |  |  |  | Property_List | R |  | Property_List | R
222
223 |  |  | Objekttyp, Property | Zuständ | PropSort | Objekttyp, Property | Vorgabe | geprüft | Objekttyp, Property | Vorgabe | geprüft
224 |  |  | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
225 | 0 | BO | Binary Output |  |  | Binary Output |  |  | Binary Output
226 | 1 | BO | Object_Identifier | U | a71 | Object_Identifier | R |  | Object_Identifier | R
227 | 2 | BO | Object_Name | B | a11 | Object_Name | R |  | Object_Name | R
228 | 3 | BO | Object_Type | B | a13 | Object_Type | R |  | Object_Type | R
229 | 4 | BO |  |  |  | Present_Value | W1 |  | Present_Value | W1
230 | 5 | BO | Description | B | a12 | Description | W |  | Description | W
231 | 6 | BO |  |  |  | Device_Type | R |  | Device_Type | R
232 | 7 | BO |  |  |  | Status_Flags | R |  | Status_Flags | R
233 | 8 | BO |  |  |  | Event_State | R |  | Event_State | R
234 | 9 | BO |  |  |  | Reliability | W1 |  | Reliability | W1
235 | 10 | BO |  |  |  | Out_Of_Service | W |  | Out_Of_Service | W
236 | 11 | BO | Polarity | B | b12 | Polarity | R |  | Polarity | R
237 | 12 | BO | Inactive_Text | B | b13 | Inactive_Text | R |  | Inactive_Text | R
238 | 13 | BO | Active_Text | B | b14 | Active_Text | R |  | Active_Text | R
239 | 14 | BO |  |  |  | Change_Of_State_Time | R |  | Change_Of_State_Time | R
240 | 15 | BO |  |  |  | Change_Of_State_Count | R0 |  | Change_Of_State_Count | R0
241 | 16 | BO |  |  |  | Time_Of_State_Count_Reset | R |  | Time_Of_State_Count_Reset | R
242 | 17 | BO |  |  |  | Elapsed_Active_Time | R0 |  | Elapsed_Active_Time | R0
243 | 18 | BO |  |  |  | Time_Of_Active_Time_Reset | R |  | Time_Of_Active_Time_Reset | R
244 | 19 | BO | Minimum_Off_Time | P | b43 | Minimum_Off_Time | R |  | Minimum_Off_Time | R
245 | 20 | BO | Minimum_On_Time | P | b44 | Minimum_On_Time | R |  | Minimum_On_Time | R
246 | 21 | BO |  |  |  | Priority_Array | R |  | Priority_Array | R
247 | 22 | BO | Relinquish_Default | B | b16 | Relinquish_Default | W |  | Relinquish_Default | W
248 | 23 | BO | Time_Delay | P | c43 | Time_Delay | W |  | Time_Delay | W
249 | 24 | BO | Notification_Class | B | c11 | Notification_Class | W |  | Notification_Class | W
250 | 25 | BO | Feedback_Value | B | c19 | Feedback_Value | R |  | Feedback_Value | R
251 | 26 | BO | Event_Enable | B | c12 | Event_Enable | W |  | Event_Enable | W
252 | 27 | BO |  |  |  | Acked_Transitions | R |  | Acked_Transitions | R
253 | 28 | BO | Notify_Type | B | c13 | Notify_Type | W |  | Notify_Type | W
254 | 29 | BO |  |  |  | Event_Time_Stamps | R |  | Event_Time_Stamps | R
255 | 30 | BO |  |  |  | Event_Message_Texts | R |  | Event_Message_Texts | R
256 | 31 | BO | Event_Message_Texts_Config | B | c14 | Event_Message_Texts_Conf | W |  | Event_Message_Texts_Config | W
257 | 32 | BO | Event_Detection_Enable | B | c15 | Event_Detection_Enable | W |  | Event_Detection_Enable | W
258 | 33 | BO | Event_Algorithm_Inhibit_Ref | P | c42 | Event_Algorithm_Inhibit_Ref | RA |  | Event_Algorithm_Inhibit_Ref | RA
259 | 34 | BO | Event_Algorithm_Inhibit | P | c41 | Event_Algorithm_Inhibit | RA |  | Event_Algorithm_Inhibit | RA
260 | 35 | BO | Time_Delay_Normal | P | c44 | Time_Delay_Normal | W |  | Time_Delay_Normal | W
261 | 36 | BO |  |  |  | Reliability_Evaluation_Inhibit | RX¦O |  | Reliability_Evaluation_Inhibit | RX¦O
262 | 37 | BO |  |  |  | Property_List | R |  | Property_List | R
263 | 38 | BO |  |  |  | Current_Command_Priority | R22 |  | Current_Command_Priority | R22
264
265 |  |  | Objekttyp, Property | Zuständ | PropSort | Objekttyp, Property | Vorgabe | geprüft | Objekttyp, Property | Vorgabe | geprüft
266 |  |  | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
267 | 0 | BV | Binary Value |  |  | Binary Value |  |  | Binary Value
268 | 1 | BV | Object_Identifier | U | a71 | Object_Identifier | R |  | Object_Identifier | R
269 | 2 | BV | Object_Name | B | a11 | Object_Name | R |  | Object_Name | R
270 | 3 | BV | Object_Type | B | a13 | Object_Type | R |  | Object_Type | R
271 | 4 | BV |  |  |  | Present_Value | W1 |  | Present_Value | W1
272 | 5 | BV | Description | B | a12 | Description | W |  | Description | W
273 | 6 | BV |  |  |  | Status_Flags | R |  | Status_Flags | R
274 | 7 | BV |  |  |  | Event_State | R |  | Event_State | R
275 | 8 | BV |  |  |  | Reliability | W1 |  | Reliability | W1
276 | 9 | BV |  |  |  | Out_Of_Service | W |  | Out_Of_Service | W
277 | 10 | BV | Inactive_Text | B | b13 | Inactive_Text | R |  | Inactive_Text | R
278 | 11 | BV | Active_Text | B | b14 | Active_Text | R |  | Active_Text | R
279 | 12 | BV |  |  |  | Change_Of_State_Time | R |  | Change_Of_State_Time | R
280 | 13 | BV |  |  |  | Change_Of_State_Count | R0 |  | Change_Of_State_Count | R0
281 | 14 | BV |  |  |  | Time_Of_State_Count_Reset | R |  | Time_Of_State_Count_Reset | R
282 | 15 | BV |  |  |  | Elapsed_Active_Time | R0 |  | Elapsed_Active_Time | R0
283 | 16 | BV |  |  |  | Time_Of_Active_Time_Reset | R |  | Time_Of_Active_Time_Reset | R
284 | 17 | BV | Minimum_Off_Time | P | b43 | Minimum_Off_Time | W |  | Minimum_Off_Time | W
285 | 18 | BV | Minimum_On_Time | P | b44 | Minimum_On_Time | W |  | Minimum_On_Time | W
286 | 19 | BV |  |  |  | Priority_Array | R |  | Priority_Array | R
287 | 20 | BV | Relinquish_Default | B | b16 | Relinquish_Default | W |  | Relinquish_Default | W
288 | 21 | BV | Time_Delay | P | c43 | Time_Delay | W |  | Time_Delay | W
289 | 22 | BV | Notification_Class | B | c11 | Notification_Class | W |  | Notification_Class | W
290 | 23 | BV | Alarm_Value | B | c16 | Alarm_Value | W |  | Alarm_Value | W
291 | 24 | BV | Event_Enable | B | c12 | Notify_Type | W |  | Event_Enable | W
292 | 25 | BV |  |  |  | Event_Time_Stamps | R |  | Acked_Transitions | R
293 | 26 | BV | Notify_Type | B | c13 | Notify_Type | W |  | Notify_Type | W
294 | 27 | BV |  |  |  | Event_Time_Stamps | R |  | Event_Time_Stamps | R
295 | 28 | BV |  |  |  | Event_Message_Texts | R |  | Event_Message_Texts | R
296 | 29 | BV | Event_Message_Texts_Config | B | c14 | Event_Message_Texts_Config | W |  | Event_Message_Texts_Config | W
297 | 30 | BV | Event_Detection_Enable | B | c15 | Event_Detection_Enable | W |  | Event_Detection_Enable | W
298 | 31 | BV | Event_Algorithm_Inhibit_Ref | P | c42 | Event_Algorithm_Inhibit_Ref | RA |  | Event_Algorithm_Inhibit_Ref | RA
299 | 32 | BV | Event_Algorithm_Inhibit | P | c41 | Event_Algorithm_Inhibit | RA |  | Event_Algorithm_Inhibit | RA
300 | 33 | BV | Time_Delay_Normal | P | c44 | Time_Delay_Normal | W |  | Time_Delay_Normal | W
301 | 34 | BV |  |  |  | Reliability_Evaluation_Inhibit | RX¦O |  | Reliability_Evaluation_Inhibit | RX¦O
302 | 35 | BV |  |  |  | Property_List | R |  | Property_List | R
303 | 36 | BV |  |  |  | Current_Command_Priority | R22 |  | Current_Command_Priority | R22
304
305 |  |  | Objekttyp, Property | Zuständ | PropSort | Objekttyp, Property | Vorgabe | geprüft | Objekttyp, Property | Vorgabe | geprüft
306 |  |  | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
307 | 0 | CAL | Calendar |  |  | Calendar |  |  | Calendar
308 | 1 | CAL | Object_Identifier | U | a71 | Object_Identifier | R |  | Object_Identifier | R
309 | 2 | CAL | Object_Name | B | a11 | Object_Name | RC |  | Object_Name | RC
310 | 3 | CAL | Object_Type | B | a13 | Object_Type | R |  | Object_Type | R
311 | 4 | CAL | Description | B | a12 | Description | W |  | Description | W
312 | 5 | CAL |  |  |  | Present_Value | R |  | Present_Value | R
313 | 6 | CAL | Date_List | B | e11 | Date_List | W |  | Date_List | W
314 | 7 | CAL |  |  |  | Property_List | R |  | Property_List | R
315
316 |  |  | Objekttyp, Property | Zuständ | PropSort | Objekttyp, Property | Vorgabe | geprüft | Objekttyp, Property | Vorgabe | geprüft
317 |  |  | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
318 | 0 | DEV | Device |  |  | Device |  |  | Device
319 | 1 | DEV | Object_Identifier | U | a71 | Object_Identifier | R |  | Object_Identifier | R
320 | 2 | DEV | Object_Name | B | a11 | Object_Name | R |  | Object_Name | R
321 | 3 | DEV | Object_Type | B | a13 | Object_Type | R |  | Object_Type | R
322 | 4 | DEV |  |  |  | System_Status | R |  | System_Status | R
323 | 5 | DEV |  |  |  | Vendor_Name | R |  | Vendor_Name | R
324 | 6 | DEV |  |  |  | Vendor_Identifier | R |  | Vendor_Identifier | R
325 | 7 | DEV |  |  |  | Model_Name | R |  | Model_Name | R
326 | 8 | DEV |  |  |  | Firmware_Revision | R |  | Firmware_Revision | R
327 | 9 | DEV |  |  |  | Application_Software_Version | R |  | Application_Software_Version | R
328 | 10 | DEV | Location | B | y11 | Location | W |  | Location | W
329 | 11 | DEV | Description | B | a12 | Description | W |  | Description | W
330 | 12 | DEV | Protocol_Version | B | y12 | Protocol_Version | R |  | Protocol_Version | R
331 | 13 | DEV | Protocol_Revision | B | y13 | Protocol_Revision | R |  | Protocol_Revision | R
332 | 14 | DEV | Protocol_Services_Supported | B | y14 | Protocol_Services_Supported | R |  | Protocol_Services_Supported | R
333 | 15 | DEV | Protocol_Object_Types_Supported | B | y15 | Protocol_Object_Types_Supported | R |  | Protocol_Object_Types_Supported | R
334 | 16 | DEV |  |  |  | Object_List | R |  | Object_List | R
335 | 17 | DEV |  |  |  | Max_APDU_Length_Accepted | W |  | Max_APDU_Length_Accepted | W
336 | 18 | DEV |  |  |  | Segmentation_Supported | R |  | Segmentation_Supported | R
337 | 19 | DEV |  |  |  | Max_Segments_Accepted | R |  | Max_Segments_Accepted | R
338 | 20 | DEV |  |  |  | Local_Time | R |  | Local_Time | R
339 | 21 | DEV |  |  |  | Local_Date | R |  | Local_Date | R
340 | 22 | DEV | UTC_Offset | B | y16 | UTC_Offset | W |  | UTC_Offset | W
341 | 23 | DEV |  |  |  | Daylight_Savings_Status | R |  | Daylight_Savings_Status | R
342 | 24 | DEV |  |  |  | APDU_Segment_Timeout | W |  | APDU_Segment_Timeout | W
343 | 25 | DEV |  |  |  | APDU_Timeout | W |  | APDU_Timeout | W
344 | 26 | DEV |  |  |  | Number_Of_APDU_Retries | R |  | Number_Of_APDU_Retries | R
345 | 27 | DEV | Time_Synchronization_Recipients | B | y18 | Time_Synchronization_Recipients | W |  | Time_Synchronization_Recipients | W
346 | 28 | DEV | Max_Master | B | y22 | Max_Master **** | W |  | Max_Master **** | W
347 | 29 | DEV | Max_Info_Frames | B | y23 | Max_Info_Frames **** | W |  | Max_Info_Frames **** | W
348 | 30 | DEV |  |  |  | Device_Address_Binding | R |  | Device_Address_Binding | R
349 | 31 | DEV |  |  |  | Database_Revision | R |  | Database_Revision | R
350 | 32 | DEV |  |  |  | Configuration_Files | R |  | Configuration_Files | R
351 | 33 | DEV |  |  |  | Last_Restore_Time | R |  | Last_Restore_Time | R
352 | 34 | DEV |  |  |  | Backup_Failure_Timeout | R |  | Backup_Failure_Timeout | R
353 | 35 | DEV |  |  |  | Backup_Preparation_Time | R |  | Backup_Preparation_Time | R
354 | 36 | DEV |  |  |  | Restore_Preparation_Time | R |  | Restore_Preparation_Time | R
355 | 37 | DEV |  |  |  | Restore_Completion_Time | R |  | Restore_Completion_Time | R
356 | 38 | DEV |  |  |  | Backup_And_Restore_State | R |  | Backup_And_Restore_State | R
357 | 39 | DEV |  |  |  | Active_COV_Subscriptions | R |  | Active_COV_Subscriptions | R
358 | 40 | DEV |  |  |  | Last_Restart_Reason | R |  | Last_Restart_Reason | R
359 | 41 | DEV |  |  |  | Time_Of_Device_Restart | R |  | Time_Of_Device_Restart | R
360 | 42 | DEV |  |  |  | Restart_Notification_Recipients | R |  | Restart_Notification_Recipients | R
361 | 43 | DEV | UTC_Time_Synchronization_Recipients | B | y17 | UTC_Time_Synchronization_Recipients | W |  | UTC_Time_Synchronization_Recipients | W
362 | 44 | DEV | Time_Synchronization_Interval | B | y19 | Time_Synchronization_Interval | W |  | Time_Synchronization_Interval | W
363 | 45 | DEV | Align_Intervals | B | y20 | Align_Intervals | W |  | Align_Intervals | W
364 | 46 | DEV | Interval_Offset | B | y21 | Interval_Offset | W |  | Interval_Offset | W
365 | 47 | DEV |  |  |  | Serial_Number | R |  | Serial_Number | R
366 | 48 | DEV |  |  |  | Property_List | R |  | Property_List | R
367
368 |  |  | Objekttyp, Property | Zuständ | PropSort | Objekttyp, Property | Vorgabe | geprüft | Objekttyp, Property | Vorgabe | geprüft
369 |  |  | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
370 | 0 | EE | Event Enrollment |  |  | Event Enrollment |  |  | Event Enrollment
371 | 1 | EE | Object_Identifier | U | a71 | Object_Identifier | R |  | Object_Identifier | R
372 | 2 | EE | Object_Name | B | a11 | Object_Name | RC |  | Object_Name | RC
373 | 3 | EE | Object_Type | B | a13 | Object_Type | R |  | Object_Type | R
374 | 4 | EE | Description | B | a12 | Description | W |  | Description | W
375 | 5 | EE | Event_Type | B | c23 | Event_Type | W |  | Event_Type | W
376 | 6 | EE | Notify_Type | B | c13 | Notify_Type | W |  | Notify_Type | W
377 | 7 | EE | Event_Parameters | B | c24 | Event_Parameters | W |  | Event_Parameters | W
378 | 8 | EE | Object_Property_Reference | P | c51 | Object_Property_Reference | W |  | Object_Property_Reference | W
379 | 9 | EE |  |  |  | Event_State | R |  | Event_State | R
380 | 10 | EE | Event_Enable | B | c12 | Event_Enable | W |  | Event_Enable | W
381 | 11 | EE |  |  |  | Acked_Transitions | R |  | Acked_Transitions | R
382 | 12 | EE | Notification_Class | B | c11 | Notification_Class | W |  | Notification_Class | W
383 | 13 | EE |  |  |  | Event_Time_Stamps | R |  | Event_Time_Stamps | R
384 | 14 | EE |  |  |  | Event_Message_Texts | R |  | Event_Message_Texts | R
385 | 15 | EE | Event_Message_Texts_Config | B | c14 | Event_Message_Texts_Conf | W |  | Event_Message_Texts_Config | W
386 | 16 | EE | Event_Detection_Enable | B | c15 | Event_Detection_Enable | W |  | Event_Detection_Enable | W
387 | 17 | EE | Event_Algorithm_Inhibit_Ref | P | c42 | Event_Algorithm_Inhibit_Ref | RA |  | Event_Algorithm_Inhibit_Ref | RA
388 | 18 | EE | Event_Algorithm_Inhibit | P | c41 | Event_Algorithm_Inhibit | RA |  | Event_Algorithm_Inhibit | RA
389 | 19 | EE | Time_Delay_Normal | P | c44 | Time_Delay_Normal | W |  | Time_Delay_Normal | W
390 | 20 | EE |  |  |  | Status_Flags | R |  | Status_Flags | R
391 | 21 | EE |  |  |  | Reliability | W1 |  | Reliability | W1
392 | 22 | EE |  |  |  | Reliability_Evaluation_Inhibit | RX¦O |  | Reliability_Evaluation_Inhibit | RX¦O
393 | 23 | EE |  |  |  | Property_List | R |  | Property_List | R
394
395 |  |  | Objekttyp, Property | Zuständ | PropSort | Objekttyp, Property | Vorgabe | geprüft | Objekttyp, Property | Vorgabe | geprüft
396 |  |  | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
397 | 0 | FL | File |  |  | File |  |  | File
398 | 1 | FL | Object_Identifier | U | a71 | Object_Identifier | R |  | Object_Identifier | R
399 | 2 | FL | Object_Name | B | a11 | Object_Name | R |  | Object_Name | R
400 | 3 | FL | Object_Type | B | a13 | Object_Type | R |  | Object_Type | R
401 | 4 | FL | Description | B | a12 | Description | W |  | Description | W
402 | 5 | FL |  |  |  | File_Type | R |  | File_Type | R
403 | 6 | FL |  |  |  | File_Size | R |  | File_Size | R
404 | 7 | FL |  |  |  | Modification_Date | R |  | Modification_Date | R
405 | 8 | FL |  |  |  | Archive | W |  | Archive | W
406 | 9 | FL |  |  |  | Read_Only | R |  | Read_Only | R
407 | 10 | FL |  |  |  | File_Access_Method | R |  | File_Access_Method | R
408 | 11 | FL |  |  |  | Property_List | R |  | Property_List | R
409
410 |  |  | Objekttyp, Property | Zuständ | PropSort | Objekttyp, Property | Vorgabe | geprüft | Objekttyp, Property | Vorgabe | geprüft
411 |  |  | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
412 | 0 | LP | Loop |  |  | Loop |  |  | Loop
413 | 1 | LP | Object_Identifier | U | a71 | Object_Identifier | R |  | Object_Identifier | R
414 | 2 | LP | Object_Name | B | a11 | Object_Name | R |  | Object_Name | R
415 | 3 | LP | Object_Type | B | a13 | Object_Type | R |  | Object_Type | R
416 | 4 | LP |  |  |  | Present_Value | W1 |  | Present_Value | W1
417 | 5 | LP | Description | B | a12 | Description | W |  | Description | W
418 | 6 | LP |  |  |  | Status_Flags | R |  | Status_Flags | R
419 | 7 | LP |  |  |  | Event_State | R |  | Event_State | R
420 | 8 | LP |  |  |  | Reliability | R |  | Reliability | R
421 | 9 | LP |  |  |  | Out_Of_Service | W |  | Out_Of_Service | W
422 | 10 | LP |  |  |  | Update_Interval | R |  | Update_Interval | R
423 | 11 | LP | Output_Units | P | f47 | Output_Units | R |  | Output_Units | R
424 | 12 | LP | Manipulated_Variable_ Reference | P | f46 | Manipulated_Variable_Reference | R |  | Manipulated_Variable_Reference | R
425 | 13 | LP | Controlled_Variable_ Reference | P | f42 | Controlled_Variable_ Reference | R |  | Controlled_Variable_Reference | R
426 | 14 | LP |  |  |  | Controlled_Variable_Value | R |  | Controlled_Variable_Value | R
427 | 15 | LP | Controlled_Variable_Units | P | f43 | Controlled_Variable_Units | R |  | Controlled_Variable_Units | R
428 | 16 | LP | Setpoint_Reference | B | f11 | Setpoint_Reference | R |  | Setpoint_Reference | R
429 | 17 | LP |  |  |  | Setpoint | R |  | Setpoint | R
430 | 18 | LP | Action | P | f41 | Action | W |  | Action | W
431 | 19 | LP | Proportional_Constant | U | f71 | Proportional_Constant | W |  | Proportional_Constant | W
432 | 20 | LP | Proportional_Constant_Units | U | f72 | Proportional_Constant_Units | R |  | Proportional_Constant_Units | R
433 | 21 | LP | Integral_Constant | U | f75 | Integral_Constant | W |  | Integral_Constant | W
434 | 22 | LP | Integral_Constant_Units | U | f76 | Integral_Constant_Units | R |  | Integral_Constant_Units | R
435 | 23 | LP | Derivative_Constant | U | f73 | Derivative_Constant | W |  | Derivative_Constant | W
436 | 24 | LP | Derivative_Constant_Units | U | f74 | Derivative_Constant_Units | R |  | Derivative_Constant_Units | R
437 | 25 | LP |  |  |  | Bias | W |  | Bias | W
438 | 26 | LP | Maximum_Output | P | f45 | Maximum_Output | W |  | Maximum_Output | W
439 | 27 | LP | Minimum_Output | P | f44 | Minimum_Output | W |  | Minimum_Output | W
440 | 28 | LP | Priority_For_Writing | B | b18 | Priority_For_Writing | R |  | Priority_For_Writing | R
441 | 29 | LP | COV_Increment | B | b17 | COV_Increment | W |  | COV_Increment | W
442 | 30 | LP |  |  |  | Property_List | R |  | Property_List | R
443 | 31
457 |  |  | Objekttyp, Property | Zuständ | PropSort | Objekttyp, Property | Vorgabe | geprüft | Objekttyp, Property | Vorgabe | geprüft
458 |  |  | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
459 | 0 | MI | Multi-state Input* |  |  | Multi-state Input* |  |  | Multi-state Input*
460 | 1 | MI | Object_Identifier | U | a71 | Object_Identifier | R |  | Object_Identifier | R
461 | 2 | MI | Object_Name | B | a11 | Object_Name | R |  | Object_Name | R
462 | 3 | MI | Object_Type | B | a13 | Object_Type | R |  | Object_Type | R
463 | 4 | MI |  |  |  | Present_Value | W1 |  | Present_Value | W1
464 | 5 | MI | Description | B | a12 | Description | W |  | Description | W
465 | 6 | MI |  |  |  | Device_Type | R |  | Device_Type | R
466 | 7 | MI |  |  |  | Status_Flags | R |  | Status_Flags | R
467 | 8 | MI |  |  |  | Event_State | R |  | Event_State | R
468 | 9 | MI |  |  |  | Reliability | W1 |  | Reliability | W1
469 | 10 | MI |  |  |  | Out_Of_Service | W |  | Out_Of_Service | W
470 | 11 | MI | Number_Of_States | P | b42 | Number_Of_States | R |  | Number_Of_States | R
471 | 12 | MI | State_Text | B | b15 | State_Text | R |  | State_Text | R
472 | 13 | MI | Time_Delay | P | c43 | Time_Delay | W |  | Time_Delay | W
473 | 14 | MI | Notification_Class | B | c11 | Notification_Class | W |  | Notification_Class | W
474 | 15 | MI | Alarm_Values | B | c17 | Alarm_Values | W |  | Alarm_Values | W
475 | 16 | MI | Fault_Values | B | c18 | Fault_Values | W |  | Fault_Values | W
476 | 17 | MI | Event_Enable | B | c12 | Event_Enable | W |  | Event_Enable | W
477 | 18 | MI |  |  |  | Acked_Transitions | R |  | Acked_Transitions | R
478 | 19 | MI | Notify_Type | B | c13 | Notify_Type | W |  | Notify_Type | W
479 | 20 | MI |  |  |  | Event_Time_Stamps | R |  | Event_Time_Stamps | R
480 | 21 | MI |  |  |  | Event_Message_Texts | R |  | Event_Message_Texts | R
481 | 22 | MI | Event_Message_Texts_Config | B | c14 | Event_Message_Texts_Conf | W |  | Event_Message_Texts_Config | W
482 | 23 | MI | Event_Detection_Enable | B | c15 | Event_Detection_Enable | W |  | Event_Detection_Enable | W
483 | 24 | MI | Event_Algorithm_Inhibit_Ref | P | c42 | Event_Algorithm_Inhibit_Ref | RA |  | Event_Algorithm_Inhibit_Ref | RA
484 | 25 | MI | Event_Algorithm_Inhibit | P | c41 | Event_Algorithm_Inhibit | RA |  | Event_Algorithm_Inhibit | RA
485 | 26 | MI | Time_Delay_Normal | P | c44 | Time_Delay_Normal | W |  | Time_Delay_Normal | W
486 | 27 | MI |  |  |  | Reliability_Evaluation_Inhibit | RX¦O |  | Reliability_Evaluation_Inhibit | RX¦O
487 | 28 | MI |  |  |  | Property_List | R |  | Property_List | R
488
489 |  |  | Objekttyp, Property | Zuständ | PropSort | Objekttyp, Property | Vorgabe | geprüft | Objekttyp, Property | Vorgabe | geprüft
490 |  |  | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
491 | 0 | MO | Multi-state Output* |  |  | Multi-state Output* |  |  | Multi-state Output*
492 | 1 | MO | Object_Identifier | U | a71 | Object_Identifier | R |  | Object_Identifier | R
493 | 2 | MO | Object_Name | B | a11 | Object_Name | R |  | Object_Name | R
494 | 3 | MO | Object_Type | B | a13 | Object_Type | R |  | Object_Type | R
495 | 4 | MO |  |  |  | Present_Value | W1 |  | Present_Value | W1
496 | 5 | MO | Description | B | a12 | Description | W |  | Description | W
497 | 6 | MO |  |  |  | Device_Type | R |  | Device_Type | R
498 | 7 | MO |  |  |  | Status_Flags | R |  | Status_Flags | R
499 | 8 | MO |  |  |  | Event_State | R |  | Event_State | R
500 | 9 | MO |  |  |  | Reliability | W1 |  | Reliability | W1
501 | 10 | MO |  |  |  | Out_Of_Service | W |  | Out_Of_Service | W
502 | 11 | MO | Number_Of_States | P | b42 | Number_Of_States | R |  | Number_Of_States | R
503 | 12 | MO | State_Text | B | b15 | State_Text | R |  | State_Text | R
504 | 13 | MO |  |  |  | Priority_Array | R |  | Priority_Array | R
505 | 14 | MO | Relinquish_Default | B | b16 | Relinquish_Default | W |  | Relinquish_Default | W
506 | 15 | MO | Time_Delay | P | c43 | Time_Delay | W |  | Time_Delay | W
507 | 16 | MO | Notification_Class | B | c11 | Notification_Class | W |  | Notification_Class | W
508 | 17 | MO | Feedback_Value | B | c19 | Feedback_Value | R |  | Feedback_Value | R
509 | 18 | MO | Event_Enable | B | c12 | Event_Enable | W |  | Event_Enable | W
510 | 19 | MO |  |  |  | Acked_Transitions | R |  | Acked_Transitions | R
511 | 20 | MO | Notify_Type | B | c13 | Notify_Type | W |  | Notify_Type | W
512 | 21 | MO |  |  |  | Event_Time_Stamps | R |  | Event_Time_Stamps | R
513 | 22 | MO |  |  |  | Event_Message_Texts | R |  | Event_Message_Texts | R
514 | 23 | MO | Event_Message_Texts_Config | B | c14 | Event_Message_Texts_Conf | W |  | Event_Message_Texts_Conf | W
515 | 24 | MO | Event_Detection_Enable | B | c15 | Event_Detection_Enable | W |  | Event_Detection_Enable | W
516 | 25 | MO | Event_Algorithm_Inhibit_Ref | P | c42 | Event_Algorithm_Inhibit_Ref | RA |  | Event_Algorithm_Inhibit_Ref | RA
517 | 26 | MO | Event_Algorithm_Inhibit | P | c41 | Event_Algorithm_Inhibit | RA |  | Event_Algorithm_Inhibit | RA
518 | 27 | MO | Time_Delay_Normal | P | c44 | Time_Delay_Normal | W |  | Time_Delay_Normal | W
519 | 28 | MO |  |  |  | Reliability_Evaluation_Inhibit | RX¦O |  | Reliability_Evaluation_Inhibit | RX¦O
520 | 29 | MO |  |  |  | Property_List | R |  | Property_List | R
521 | 30 | MO |  |  |  | Current_Command_Priority | R22 |  | Current_Command_Priority | R22
522
523 |  |  | Objekttyp, Property | Zuständ | PropSort | Objekttyp, Property | Vorgabe | geprüft | Objekttyp, Property | Vorgabe | geprüft
524 |  |  | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
525 | 0 | MV | Multi-state Value |  |  | Multi-state Value |  |  | Multi-state Value
526 | 1 | MV | Object_Identifier | U | a71 | Object_Identifier | R |  | Object_Identifier | R
527 | 2 | MV | Object_Name | B | a11 | Object_Name | R |  | Object_Name | R
528 | 3 | MV | Object_Type | B | a13 | Object_Type | R |  | Object_Type | R
529 | 4 | MV |  |  |  | Present_Value | W1 |  | Present_Value | W1
530 | 5 | MV | Description | B | a12 | Description | W |  | Description | W
531 | 6 | MV |  |  |  | Status_Flags | R |  | Status_Flags | R
532 | 7 | MV |  |  |  | Event_State | R |  | Event_State | R
533 | 8 | MV |  |  |  | Reliability | W1 |  | Reliability | W1
534 | 9 | MV |  |  |  | Out_Of_Service | W |  | Out_Of_Service | W
535 | 10 | MV | Number_Of_States | P | b42 | Number_Of_States | R |  | Number_Of_States | R
536 | 11 | MV | State_Text | B | b15 | State_Text | R |  | State_Text | R
537 | 12 | MV |  |  |  | Priority_Array | R |  | Priority_Array | R
538 | 13 | MV | Relinquish_Default | B | b16 | Relinquish_Default | W |  | Relinquish_Default | W
539 | 14 | MV | Time_Delay | P | c43 | Time_Delay | W |  | Time_Delay | W
540 | 15 | MV | Notification_Class | B | c11 | Notification_Class | W |  | Notification_Class | W
541 | 16 | MV | Alarm_Values | B | c17 | Alarm_Values | W |  | Alarm_Values | W
542 | 17 | MV | Fault_Values | B | c18 | Fault_Values | W |  | Fault_Values | W
543 | 18 | MV | Event_Enable | B | c12 | Event_Enable | W |  | Event_Enable | W
544 | 19 | MV |  |  |  | Acked_Transitions | R |  | Acked_Transitions | R
545 | 20 | MV | Notify_Type | B | c13 | Notify_Type | W |  | Notify_Type | W
546 | 21 | MV |  |  |  | Event_Time_Stamps | R |  | Event_Time_Stamps | R
547 | 22 | MV |  |  |  | Event_Message_Texts | R |  | Event_Message_Texts | R
548 | 23 | MV | Event_Message_Texts_Config | B | c14 | Event_Message_Texts_Conf | W |  | Event_Message_Texts_Config | W
549 | 24 | MV | Event_Detection_Enable | B | c15 | Event_Detection_Enable | W |  | Event_Detection_Enable | W
550 | 25 | MV | Event_Algorithm_Inhibit_Ref | P | c42 | Event_Algorithm_Inhibit_Ref | RA |  | Event_Algorithm_Inhibit_Ref | RA
551 | 26 | MV | Event_Algorithm_Inhibit | P | c41 | Event_Algorithm_Inhibit | RA |  | Event_Algorithm_Inhibit | RA
552 | 27 | MV | Time_Delay_Normal | P | c44 | Time_Delay_Normal | W |  | Time_Delay_Normal | W
553 | 28 | MV |  |  |  | Reliability_Evaluation_Inhibit | RX¦O |  | Reliability_Evaluation_Inhibit | RX¦O
554 | 29 | MV |  |  |  | Property_List | R |  | Property_List | R
555 | 30 | MV |  |  |  | Current_Command_Priority | R22 |  | Current_Command_Priority | R22
556
557 |  |  | Objekttyp, Property | Zuständ | PropSort | Objekttyp, Property | Vorgabe | geprüft | Objekttyp, Property | Vorgabe | geprüft
558 |  |  | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
559 | 0 | NC | Notification Class |  |  | Notification Class |  |  | Notification Class
560 | 1 | NC | Object_Identifier | U | a71 | Object_Identifier | R |  | Object_Identifier | R
561 | 2 | NC | Object_Name | B | a11 | Object_Name | RC |  | Object_Name | RC
562 | 3 | NC | Object_Type | B | a13 | Object_Type | R |  | Object_Type | R
563 | 4 | NC | Description | B | a12 | Description | W |  | Description | W
564 | 5 | NC | Notification_Class | B | c11 | Notification_Class | R |  | Notification_Class | R
565 | 6 | NC | Priority | B | c20 | Priority | W |  | Priority | W
566 | 7 | NC | Ack_Required | B | c21 | Ack_Required | W |  | Ack_Required | W
567 | 8 | NC | Recipient_List | B | c22 | Recipient_List | W |  | Recipient_List | W
568 | 9 | NC |  |  |  | Property_List | R |  | Property_List | R
569
570 |  |  | Objekttyp, Property | Zuständ | PropSort | Objekttyp, Property | Vorgabe | geprüft | Objekttyp, Property | Vorgabe | geprüft
571 |  |  | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
572 | 0 | SCH | Schedule |  |  | Schedule |  |  | Schedule
573 | 1 | SCH | Object_Identifier | U | a71 | Object_Identifier | R |  | Object_Identifier | R
574 | 2 | SCH | Object_Name | B | a11 | Object_Name | RC |  | Object_Name | RC
575 | 3 | SCH | Object_Type | B | a13 | Object_Type | R |  | Object_Type | R
576 | 4 | SCH |  |  |  | Present_Value | W1 |  | Present_Value | W1
577 | 5 | SCH | Description | B | a12 | Description | W |  | Description | W
578 | 6 | SCH | Effective_Period | B | e12 | Effective_Period | W |  | Effective_Period | W
579 | 7 | SCH | Weekly_Schedule | B | e13 | Weekly_Schedule | W |  | Weekly_Schedule | W
580 | 8 | SCH | Exception_Schedule | B | e14 | Exception_Schedule | W |  | Exception_Schedule | W
581 | 9 | SCH | Schedule_Default | B | e15 | Schedule_Default | W |  | Schedule_Default | W
582 | 10 | SCH | List_Of_Object_Property_Reference | P | e71 | List_Of_Object_Property_Reference | W |  | List_Of_Object_Property_Reference | W
583 | 11 | SCH | Priority_For_Writing | B | b18 | Priority_For_Writing | W |  | Priority_For_Writing | W
584 | 12 | SCH |  |  |  | Status_Flags | R |  | Status_Flags | R
585 | 13 | SCH |  |  |  | Reliability | W1 |  | Reliability | W1
586 | 14 | SCH |  |  |  | Out_Of_Service | W |  | Out_Of_Service | W
587 | 15 | SCH | Event_Detection_Enable | B | c15 | Event_Detection_Enable | W |  | Event_Detection_Enable | W
588 | 16 | SCH | Notification_Class | B | c11 | Notification_Class | W |  | Notification_Class | W
589 | 17 | SCH | Event_Enable | B | c12 | Event_Enable | W |  | Event_Enable | W
590 | 18 | SCH |  |  |  | Event_State | R |  | Event_State | R
591 | 19 | SCH |  |  |  | Acked_Transitions | R |  | Acked_Transitions | R
592 | 20 | SCH | Notify_Type | B | c13 | Notify_Type | W |  | Notify_Type | W
593 | 21 | SCH |  |  |  | Event_Time_Stamps | R |  | Event_Time_Stamps | R
594 | 22 | SCH |  |  |  | Event_Message_Texts | R |  | Event_Message_Texts | R
595 | 23 | SCH | Event_Message_Texts_Config | B | c14 | Event_Message_Texts_Conf | W |  | Event_Message_Texts_Config | W
596 | 24 | SCH |  |  |  | Reliability_Evaluation_Inhibit | RX¦O |  | Reliability_Evaluation_Inhibit | RX¦O
597 | 25 | SCH |  |  |  | Property_List | R |  | Property_List | R
598
599 |  |  | Objekttyp, Property | Zuständ | PropSort |  |  |  | Objekttyp, Property | Vorgabe | geprüft
600 |  |  | 1 | 2 | 3 |  |  |  | 1 | 2 | 3
601 | 0 | SV | Structured View | [5 empty] | Structured View
602 | 1 | SV | Object_Identifier | U | a71 |  |  |  | Object_Identifier | R
603 | 2 | SV | Object_Name | B | a11 |  |  |  | Object_Name | R
604 | 3 | SV | Object_Type | B | a13 |  |  |  | Object_Type | R
605 | 4 | SV | Description | B | a12 |  |  |  | Description | W
606 | 5 | SV | Node_Type | B | x11 |  |  |  | Node_Type | R
607 | 6 | SV | Node_Subtype | B | x12 |  |  |  | Node_Subtype | R
608 | 7 | SV | Subordinate_List | B | x13 |  |  |  | Subordinate_List | R
608 | 7 | SV | [6 empty] | Subordinate_Annotations | R
609 | 8 | SV | [6 empty] | Property_List | R
610
616 |  |  | Objekttyp, Property | Zuständ | PropSort | Objekttyp, Property | Vorgabe | geprüft | Objekttyp, Property | Vorgabe | geprüft
617 |  |  | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
618 | 0 | TL | Trend Log |  |  | Trend Log |  |  | Trend Log
619 | 1 | TL | Object_Identifier | U | a71 | Object_Identifier | R |  | Object_Identifier | R
620 | 2 | TL | Object_Name | B | a11 | Object_Name | RC |  | Object_Name | RC
621 | 3 | TL | Object_Type | B | a13 | Object_Type | R |  | Object_Type | R
622 | 4 | TL | Description | B | a12 | Description | W |  | Description | W
623 | 5 | TL | Enable | B | d11 | Enable | W |  | Enable | W
624 | 6 | TL |  |  |  | Start_Time | W |  | Start_Time | W
625 | 7 | TL |  |  |  | Stop_Time | W |  | Stop_Time | W
626 | 8 | TL | Log_DeviceObjectProperty | B | d12 | Log_DeviceObjectProperty | W |  | Log_DeviceObjectProperty | W
627 | 9 | TL | Log_Interval | B | d13 | Log_Interval | W |  | Log_Interval | W
628 | 10 | TL | COV_Resubscription_Interval | B | d14 | COV_Resubscription_Interval | W |  | COV_Resubscription_Interval | W
629 | 11 | TL | Client_COV_Increment | B | d15 | Client_COV_Increment | W |  | Client_COV_Increment | W
630 | 12 | TL | Stop_When_Full | B | d16 | Stop_When_Full | W |  | Stop_When_Full | W
631 | 13 | TL | Buffer_Size | B | d17 | Buffer_Size | W |  | Buffer_Size | W
632 | 14 | TL |  |  |  | Log_Buffer | R |  | Log_Buffer | R
633 | 15 | TL |  |  |  | Record_Count | W |  | Record_Count | W
634 | 16 | TL |  |  |  | Total_Record_Count | R |  | Total_Record_Count | R
635 | 17 | TL | Logging_Type | B | d18 | Logging_Type | W |  | Logging_Type | W
636 | 18 | TL | Trigger | B | d19 | Trigger | W |  | Trigger | W
637 | 19 | TL |  |  |  | Status_Flags | R |  | Status_Flags | R
638 | 20 | TL |  |  |  | Reliability | W1 |  | Reliability | W1
639 | 21 | TL | Notification_Threshold | B | d20 | Notification_Threshold | W |  | Notification_Threshold | W
640 | 22 | TL |  |  |  | Records_Since_Notification | R |  | Records_Since_Notification | R
641 | 23 | TL |  |  |  | Last_Notify_Record | R |  | Last_Notify_Record | R
642 | 24 | TL |  |  |  | Event_State | R |  | Event_State | R
643 | 25 | TL | Notification_Class | B | c11 | Notification_Class | W |  | Notification_Class | W
644 | 26 | TL | Event_Enable | B | c12 | Event_Enable | W |  | Event_Enable | W
645 | 27 | TL |  |  |  | Acked_Transitions | R |  | Acked_Transitions | R
646 | 28 | TL | Notify_Type | B | c13 | Notify_Type | R |  | Notify_Type | R
647 | 29 | TL |  |  |  | Event_Time_Stamps | R |  | Event_Time_Stamps | R
648 | 30 | TL |  |  |  | Event_Message_Texts | R |  | Event_Message_Texts | R
649 | 31 | TL | Event_Message_Texts_Config | B | c14 | Event_Message_Texts_Conf | W |  | Event_Message_Texts_Config | W
650 | 32 | TL | Event_Detection_Enable | B | c15 | Event_Detection_Enable | W |  | Event_Detection_Enable | W
651 | 33 | TL |  |  |  | Property_List | R |  | Property_List | R
611
612
613
612
612
611
613
613
612
613
652
653 | [5 empty] | Legende zu 4.
654 | [5 empty] | * Unterstützung von MI- und MO-Objekten ist für das AMEV-Testat nicht zwingend erforderlich, da die Funktionen in der AS durch einfache I/O-Objekte gleichwertig realisierbar sind.
**** entfällt bei Unterstützung von Network Port Objekt
655 | [5 empty] | X: BACnet-Gerät unterstützt BIBBs bzw. Objekttyp.
656 | [5 empty] | XT: BACnet-Gerät unterstützt nach Norm entweder DM-TS-B oder DM-UTC-B.
657 | [5 empty] | R: Property der AS kann nur gelesen werden (Norm: Required).
658 | [5 empty] | RA: Properties alternativ nutzen, d.h. ein Property auswählen.
659 | [5 empty] | RC: Property kann bei der Erzeugung einer neuen Objektinstanz in der AS mit dem Dienst CreateObject oder generell mit WriteProperty beschrieben werden (W).
660 | [5 empty] | RX: Falls Property vorhanden ist, muss der Wert "FALSE" sein.
661 | [5 empty] | RO: Zum Rücksetzen des Zählers in der AS kann das Property mit dem Wert 0 beschrieben werden.
662 | [5 empty] | R22: In Rev.16 noch nicht enthalten; ab Rev.22 nach Norm required.
663 | [5 empty] | W: Property der AS kann gelesen und überschrieben werden (Norm: Write).
664 | [5 empty] | W1: Property ist nur beschreibbar, wenn Out_Of_Service gesetzt ist.
665
611
666
667 | [5 empty] | 5. Sonstige Anforderungen an Profil AS-C und an Profil AS-D
668 | [5 empty] | Prüfbereich | Vorgabe |  |  | geprüft | Ergebnis
669 | [5 empty] | 1 |  |  | 2 | 3 | 4
670 | [5 empty] | Zertifikat | Nummer
671 | [5 empty] | Netzwerkprotokoll | mind. BACnet/IP
672 | [5 empty] | Zeichensatz | UTF-8
673 | [5 empty] | Object_Name | Mindest-Zeichenanzahl: 64
674 | [5 empty] | Description | Mindest-Zeichenanzahl: 255
675 | [5 empty] | Device_Type | Mindest-Zeichenanzahl: 64
676 | [5 empty] | Inactive_Text | Mindest-Zeichenanzahl: 32
677 | [5 empty] | Active_Text | Mindest-Zeichenanzahl: 32
678 | [5 empty] | State_Text | Mindest-Zeichenanzahl: 32 (je Zustand)
679 | [5 empty] | Event_Message_Texts_Conf | Mindest-Zeichenanzahl: 64
680 | [5 empty] | Location | Mindest-Zeichenanzahl: 64
681 | [5 empty] | Calendar Object | mind. 3 Instanzen
682 | [6 empty] | mind. 15 Datumeinträge in Date List je Instanz
683 | [5 empty] | Schedule Object | Weekly Schedule: mind. 12 Schaltzeiten (6x Ein-Aus) je Tag
684 | [6 empty] | Exception_Schedule: mind. 6 Datumeinträge
685 | [6 empty] | oder Kalender-Verweise (Kombination möglich);
686 | [6 empty] | Exception_Schedule: mind. 12 Schaltzeiten (6x Ein-Aus).
687
688
689 | [5 empty] | 6. Ergebnis |  |  |  |  | JA
690 | [5 empty] | Das BACnet-Gerät unterstützt die BACnet-Funktionen für das AMEV-Profil AS-C gemäß BACtwin 202x**
691 | [5 empty] | ** Wenn zutreffend, bitte ankreuzen im Feld unter JA.
692 | [10 empty] | JA
693 | [5 empty] | Das BACnet-Gerät unterstützt die BACnet-Funktionen für das AMEV-Profil AS-D gemäß BACtwin 202x**
694 | [5 empty] | ** Wenn zutreffend, bitte ankreuzen im Feld unter JA.
695
696
697 | [5 empty] | 7. Aufgestellt
698 | [5 empty] | BACnet-Zertifizierungsstelle
699
700
701 | [5 empty] | Ort, Datum
702
703
704 | [5 empty] | Name, Unterschrift

## 8.1 AI
ObjSort + LfdNr | UUID | Objekt-Template- Kennung | Kommentar | GA-FL Einträge (1.1.1) | GA-FL Einträge (2.2.1) | GA-FL Einträge (3.1.1) | GA-FL Einträge (3.1.3) | GA-FL Einträge (Abschnitte/Spalten) | Object_Name | Description | Verwendung | Status_Flags | Event_State | Reliability | Out_Of_Service | Units | Min_Pres_Value | Max_Pres_Value | Resolution | COV_Increment | Time_Delay | Notification_Class | Low_Limit | High_Limit | Deadband | Limit_Enable | Event_Enable | Notify_Type | Event_Time_Stamps | Event_Message_Texts | Event_Message_Texts_Config | Event_Detection_Enable | Event_Algorithm_Inhibit | Event_Algorithm_Inhibit_Ref | Time_Delay_Normal | Reliability_Evaluation_Inhibit | Letztmalige Änderung in Version
|  | PropSort |  | (Abschnitte/Spalten) |  |  |  |  | a11 | a12 | [5 empty] | b11 | c45 | c46 | b41 | b17 | c43 | c11 | c47 | c48 | c50 | c49 | c12 | c13 |  |  | c14 | c15 | c41 | c42 | c44
|  | Conformance Code | [6 empty] | R | W |  | R | R | W1 | W | W | R | R | R | W | W | W | W | W | W | W | W | W | R | R | W | W | RA | RA | W | RX¦O
|  | Grundlegende Vorgabe * | [6 empty] | B * | B | [5 empty] | B | P | P | P | B | P | B | P | P | P | P | B | B |  |  | B | B | P | P | P
|  | Detailierte Festlegung * | [6 empty] | P * | P | [5 empty] | P | P | P | P | P | P | P | P | P | P | P | P | P |  |  | P | P | P | P | P
|  | Umsetzung * | [6 empty] | U * | U |  | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U |  |  | U | U | U | U | U | U
|  | Vorgabewert (Parametrierung) | [6 empty] | ja | ja |  | nein | nein | nein | nein | ja | nein | nein | nein | ja | ja | ja | ja | ja | ja | ja | ja | ja | nein | nein | ja | ja | nein | nein | ja | nein
a101 | eaaa2766-7799-4761-9f2e-4b78d1135816 | AI_MW_T_AMEV1 | Temperatur | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Temperatur Messwert | {f,f,f,f} | 0 | 0 | {f} | °C |  |  |  | > 0 | > 0 | festlegen | [festlegen] | [festlegen] | festlegen | festlegen | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a102 | e2dbfb8e-1c50-4955-a2ac-ce277690d32a | AI_MW_T_AU_AMEV1 | Temperatur Außen | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Temperatur Messwert | {f,f,f,f} | 0 | 0 | {f} | °C |  |  |  | 0.2 | 120 | 300 | [-20] | [40] | 0.2 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a103 | 2a8bafff-e065-492d-a95c-69fc0c7d05a9 | AI_MW_T_H_NT_AMEV1 | Heizung Niedertemperatur | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Temperatur Messwert | {f,f,f,f} | 0 | 0 | {f} | °C |  |  |  | 0.5 | 1 | 300 | [10] | [50] | 0.5 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a104 | e09e423a-dc58-4a00-aa68-605ff5a723f3 | AI_MW_T_H_HT_AMEV1 | Heizung Hochtemperatur | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Temperatur Messwert | {f,f,f,f} | 0 | 0 | {f} | °C |  |  |  | 1 | 1 | 300 | [10] | [90] | 1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a105 | d98d7856-1f80-40fb-8e3f-4c08979f8d12 | AI_MW_T_H_HW_AMEV1 | Fühler Temperatur Heißwasser | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Temperatur Messwert | {f,f,f,f} | 0 | 0 | {f} | °C |  |  |  | 1.5 | 1 | 300 | [10] | [160] | 1.5 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a106 | 0bf4a0f5-bc4d-429b-b275-da552667d731 | AI_MW_T_H_TO_AMEV1 | Fühler Temperatur Thermo-Öl | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Temperatur Messwert | {f,f,f,f} | 0 | 0 | {f} | °C |  |  |  | 3 | 1 | 300 | [0] | [300] | 3 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a107 | 0f891ba8-b1fa-4a0c-839b-8835d5cedef6 | AI_MW_T_H_WW_AMEV1 | Fühler Temperatur Warmwasser | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Temperatur Messwert | {f,f,f,f} | 0 | 0 | {f} | °C |  |  |  | 1 | 60 | 300 | [55] | [75] | 1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a108 | 2aeebe4e-219a-49ac-bfef-32e7c0a4c92a | AI_MW_T_H_AG_AMEV1 | Fühler Temperatur Abgas | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Temperatur Messwert | {f,f,f,f} | 0 | 0 | {f} | °C |  |  |  | 10 | 1 | 300 | [-20] | [1300] | 10 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a109 | c84dd10b-0288-4196-b919-1e9c9d9bd04f | AI_MW_T_L_RU_AMEV1 | Fühler Temperatur Lüftung Raum | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Temperatur Messwert | {f,f,f,f} | 0 | 0 | {f} | °C |  |  |  | 0.5 | 60 | 300 | [5] | [40] | 0.5 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a110 | 6bbad302-e8f7-4a84-b51c-3e87218c052a | AI_MW_T_L_TP_AMEV1 | Fühler Temperatur Taupunkt | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Temperatur Messwert | {f,f,f,f} | 0 | 0 | {f} | °C |  |  |  | 0.1 | 60 | 300 | [10] | [20] | 0.1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a111 | 89f8d967-9a68-4e06-9ffa-754922f88227 | AI_MW_T_K_NT_AMEV1 | Fühler Temperatur Kälte Niedertemperatur | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Temperatur Messwert | {f,f,f,f} | 0 | 0 | {f} | °C |  |  |  | 0.1 | 60 | 300 | [4] | [14] | 0.1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a112 | 718ad974-af2f-4146-96d6-bea00ea74ada | AI_MW_T_K_HT_AMEV1 | Fühler Temperatur Kälte Hochtemperatur | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Temperatur Messwert | {f,f,f,f} | 0 | 0 | {f} | °C |  |  |  | 0.1 | 60 | 300 | [12] | [22] | 0.1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a113 | b3817b71-21f4-4bfe-9a74-a37195f8dc96 | AI_MW_T_K_KW_AMEV1 | Fühler Temperatur Kaltwasser | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Temperatur Messwert | {f,f,f,f} | 0 | 0 | {f} | °C |  |  |  | 0.5 | 60 | 300 | [-20] | [45] | 0.5 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a114 | c2767d39-1a7a-4f31-8158-1065f295e22b | AI_MW_X_L_RU_AMEV1 | Fühler Feuchte absolut Raum | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Feuchte absolut Messwert | {f,f,f,f} | 0 | 0 | {f} | g/m³ |  |  |  | 0.1 | 240 | 300 | [4] | [11,5] | 0.1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a115 | bac01cca-6d06-4acf-a53c-aee331c70ada | AI_MW_X_L_AU_AMEV1 | Fühler Feuchte absolut Außen | X |  | X | X | 1.1.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Feuchte absolut Messwert | {f,f,f,f} | 0 | 0 | {f} | g/m³ |  |  |  | 0.1 | [5 empty] | {f,f} | {t,t,t} | Alarm | * | * | *** | {f} |  |  | 1
a116 | 58a3cfc8-1796-4d99-9fa6-78f30119deb1 | AI_MW_M_L_RU_AMEV1 | Fühler Feuchte 0-100% r.F.Raum | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Feuchte relativ Messwert | {f,f,f,f} | 0 | 0 | {f} | %r.F. |  |  |  | 3 | 240 | 300 | [30] | [70] | 3 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a117 | 075de54e-3d27-47c5-93d5-d49f53d9a47a | AI_MW_M_L_AU_AMEV1 | Fühler Feuchte 0-100% r.F.Außen | X |  | X | X | 1.1.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Feuchte relativ Messwert | {f,f,f,f} | 0 | 0 | {f} | %r.F. |  |  |  | 3 | [5 empty] | {f,f} | {t,t,t} | Alarm | * | * | *** | {f} |  |  | 1
a118 | d4eb029a-afde-49be-8433-a80e9836e0ff | AI_MW_P_AMEV1 | Fühler Druck | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Druck Messwert | {f,f,f,f} | 0 | 0 | {f} | Pa |  |  |  | festlegen | festlegen | 300 | [festlegen] | [festlegen] | [festlegen] | festlegen | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a119 | 2fa98944-1523-4d24-b54f-5ad56518f119 | AI_MW_P_GAS_AMEV1 | Fühler Druck Gas (z.B. Erdgas, techn. Gase) | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Druck Messwert | {f,f,f,f} | 0 | 0 | {f} | mbar |  |  |  | festlegen | festlegen | 300 | [festlegen] | [festlegen] | [festlegen] | festlegen | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a120 | a91696d3-f510-49ff-8e26-a74b81b1f383 | AI_MW_P_GM_AMEV1 | Fühler Druck Gas Gefahrmeldung (siehe NC100) | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Druck Messwert | {f,f,f,f} | 0 | 0 | {f} | mbar |  |  |  | festlegen | festlegen | 100 | [festlegen] | [festlegen] | [festlegen] | festlegen | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a121 | 5fa7e6c7-9fdc-404e-aa3e-6417d5b9e94c | AI_MW_P_L_AMEV1 | Fühler Druck 0-1000Pa Lüftung | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Druck Messwert | {f,f,f,f} | 0 | 0 | {f} | Pa |  |  |  | [30] | 120 | 300 | [0] | [500] | [30] | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a122 | 063cbe52-fcf7-4c05-8ac5-c61e10a26ef1 | AI_MW_P_Tem_AMEV1 | Fühler Druck 0-10bar Heizung | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Druck Messwert | {f,f,f,f} | 0 | 0 | {f} | bar |  |  |  | 0.1 | 30 | 300 | [1,5] | [5] | 0.1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a123 | d4a75ac9-4226-4ca5-a049-5c6b1a48ca19 | AI_MW_PD_L_AMEV1 | Fühler Differenzdruck 0-5000/(+-50 Ringwaage)Pa Differenzdruck Lüftung | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Druck Differenz Messwert | {f,f,f,f} | 0 | 0 | {f} | Pa |  |  |  | [150/3] | 120 | 300 | [0/-40] | [500/40] | [150/3] | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1/120
a124 | b482754f-25a2-4a8a-ad5d-65d5ffeed0fc | AI_MW_PD_Tem_AMEV1 | Fühler Differenzdruck 0-5,5bar Differenzdruck Heizung | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Druck Differenz Messwert | {f,f,f,f} | 0 | 0 | {f} | bar |  |  |  | 0.1 | 30 | 300 | [1,5] | [5] | 0.1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a125 | 3f1625fa-e598-4fa7-982b-377758f2c97a | AI_MW_F_AMEV1 | Fühler Volumenstrom Zähler, Volumenstromregler | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Volumenstrom Messwert | {f,f,f,f} | 0 | 0 | {f} | m3/h |  |  |  | festlegen | festlegen | 300 | [festlegen] | [festlegen] |  | festlegen | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a126 | 1b7596c2-69b1-4383-ab31-f892b6a661be | AI_MW_J_AMEV1 | Fühler Leistung Zähler | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Leistung Messwert | {f,f,f,f} | 0 | 0 | {f} | kW |  |  |  | festlegen | festlegen | 300 | [festlegen] | [festlegen] |  | festlegen | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a127 | 862891c7-7141-40fa-aec2-a39790b15134 | AI_MW_QCD_AMEV1 | Fühler CO2 Kohlendioxid | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | CO2 Messwert | {f,f,f,f} | 0 | 0 | {f} | ppm |  |  |  | 50 | 3600 | 300 | [400] | [1200] | 50 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a128 | 53735a65-bd13-4a65-be6d-9d62908c3222 | AI_MW_QCO_AMEV1 | Fühler CO Kohlenmonoxid | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | CO Messwert | {f,f,f,f} | 0 | 0 | {f} | ppm |  |  |  | [1] | 3600 | 200 | [0] | [30] | 1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a129 | c74b246d-5eaf-45cd-92c7-f6807bb391e1 | AI_MW_QPH_AMEV1 | Fühler Leitfähigkeit | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | PH Messwert | {f,f,f,f} | 0 | 0 | {f} | pH |  |  |  | [0,1] | 3600 | 300 | [6] | [8] | [0,1] | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a130 | d9d0c12a-b62a-4162-8a40-fd93b517bbb9 | AI_MW_E_RU_AMEV1 | Fühler Beleuchtungsstärke Raum | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Beleuchtungsstärke Messwert | {f,f,f,f} | 0 | 0 | {f} | lx |  |  |  | 50 | 3600 | 300 | 0 | [1000] | 50 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a131 | f46a9485-9ca6-4280-8f39-afd9551ad445 | AI_MW_E_AU_AMEV1 | Fühler Beleuchtungsstärke Außen | X |  | X | X | 1.1.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Beleuchtungsstärke Messwert | {f,f,f,f} | 0 | 0 | {f} | lx |  |  |  | 50 | 3600 | 300 |  |  |  | {f,f} | {f,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a132 | d8968258-1895-4231-8956-6738f46688c4 | AI_MW_R_AU_AMEV1 | Fühler Globalstrahlung Außen | X |  | X | X | 1.1.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Globalstrahlung Messwert | {f,f,f,f} | 0 | 0 | {f} | W/m² |  |  |  | 50 | 3600 | 300 |  |  |  | {f,f} | {f,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a133 | ef55d7b8-8592-4705-8401-774c060d4164 | AI_MW_L_AMEV1 | Fühler Füllstand (Level) | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Füllstand Messwert | {f,f,f,f} | 0 | 0 | {f} | [%] |  |  |  | [0,5] | 3600 | 300 | [20] | [100] | [1] | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a134 | 0f3b5b89-35fb-4100-b47d-2678f1a01963 | AI_RW_AMEV1 | Rückführwert | X |  | X | X | 1.1.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Rückführwert | {f,f,f,f} | 0 | 0 | {f} | % |  |  |  | 3 | 60 | 300 | [0] | [100] | 3 | {f,f} | {f,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a135 | 894896d3-a42d-46ae-88ac-d1f9ab231be2 | AI_MW_WIG_AMEV1 | Fühler thermisches Anemometer/Sternanemometer | X |  | X | X | 1.1.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Windgeschwindigkeit Messwert | {f,f,f,f} | 0 | 0 | {f} | m/s |  |  |  | 0.1 | 60 | 300 |  |  |  | {f,f} | {f,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a136 | 32295474-6ba0-497e-8121-d779093ab883 | AI_MW_RW_AMEV1 | Leistungsrückmeldung | X |  | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Leistung Rückführwert | {f,f,f,f} | 0 | 0 | {f} | % |  |  |  | 3 | 60 | 300 | [0] | [100] | 3 | {f,f} | {f,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a137 | 14a47d97-ef24-4ff2-a394-e0047149b373 | AI_MW_LTF_AMEV1 | Leitfähigkeit | X |  | X | X | 1.1.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Leitfähigkeit Messwert | {f,f,f,f} | 0 | 0 | {f} | S/m |  |  |  | [0,1] | 60 | 300 |  |  |  | {f,f} | {f,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a138 | bd849768-c7e4-4d4c-8a99-ab5942a2bfb2 | AI_SW_J_AMEV1 | Sollwert Leistung (Einspeisung) | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Leistung Sollwert | {f,f,f,f} | 0 | 0 | {f} | % |  |  |  | festlegen | festlegen | 300 | [festlegen] | [festlegen] |  | festlegen | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
|  | * B (Bauherr/Betreiber), P (GA-Planung), U (Ausführendes Unternehmen) | [6 empty] | Vorgabewert (Parametrierung) und Prüfwert | [10 empty] | [] => Default-Werte (Vorschlag) | [7 empty] | * Kann zur Prüfung beim 1:1 Test verwendet werden
[9 empty] | Prüfwert (systemintern erzeugter Wert) | [21 empty] | *** gemäß Kapitel 4.4 einrichten
ENGLISH VERSION (Draft)
ObjSort + No. | UUID | Object Template Identifier | Comment | BACS FL entries (1.1.1) | BACS FL entries (2.2.1) | BACS FL entries (3.1.1) | BACS FL entries (3.1.3) | BACS Function List entries (sections/columns) | Object_Name | Description | Application | Status_Flags | Event_State | Reliability | Out_Of_Service | Units | Min_Pres_Value | Max_Pres_Value | Resolution | COV_Increment | Time_Delay | Notification_Class | Low_Limit | High_Limit | Deadband | Limit_Enable | Event_Enable | Notify_Type | Event_Time_Stamps | Event_Message_Texts | Event_Message_Texts_Config | Event_Detection_Enable | Event_Algorithm_Inhibit | Event_Algorithm_Inhibit_Ref | Time_Delay_Normal | Reliability_Evaluation_Inhibit | Last change in version
|  | PropSort | [6 empty] | a11 | a12 | [5 empty] | b11 | c45 | c46 | b41 | b17 | c43 | c11 | c47 | c48 | c50 | c49 | c12 | c13 |  |  | c14 | c15 | c41 | c42 | c44
|  | Conformance Code | [6 empty] | R | W |  | R | R | W1 | W | W | R | R | R | W | W | W | W | W | W | W | W | W | R | R | W | W | RA | RA | W | RX¦O
|  | Basic spezification * | [6 empty] | B * | B | [5 empty] | B | P | P | P | B | P | B | P | P | P | P | B | B |  |  | B | B | P | P | P
|  | Detailed definition * | [6 empty] | P * | P | [5 empty] | P | P | P | P | P | P | P | P | P | P | P | P | P |  |  | P | P | P | P | P
|  | Implementation * | [6 empty] | X * | X |  | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X |  |  | X | X | X | X | X | X
|  | Default value (parameterization) | [6 empty] | yes | yes |  | no | no | no | no | yes | no | no | no | yes | yes | yes | yes | yes | yes | yes | yes | yes | no | no | yes | yes | no | no | yes | no
a101 | eaaa2766-7799-4761-9f2e-4b78d1135816 | AI_MW_T_AMEV1 | Temperature | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Temperature Reading | {f,f,f,f} | 0 | 0 | {f} | °C |  |  |  | > 0 | > 0 | specify | [specify] | [specify] | specify | specify | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a102 | e2dbfb8e-1c50-4955-a2ac-ce277690d32a | AI_MW_T_AU_AMEV1 | Temperature outside | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Temperature Reading | {f,f,f,f} | 0 | 0 | {f} | °C |  |  |  | 0.2 | 120 | 300 | [-20] | [40] | 0.2 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a103 | 2a8bafff-e065-492d-a95c-69fc0c7d05a9 | AI_MW_T_H_NT_AMEV1 | Heating Low Temperature | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Temperature Reading | {f,f,f,f} | 0 | 0 | {f} | °C |  |  |  | 0.5 | 1 | 300 | [10] | [50] | 0.5 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a104 | e09e423a-dc58-4a00-aa68-605ff5a723f3 | AI_MW_T_H_HT_AMEV1 | Heating High Temperature | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Temperature Reading | {f,f,f,f} | 0 | 0 | {f} | °C |  |  |  | 1 | 1 | 300 | [10] | [90] | 1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a105 | d98d7856-1f80-40fb-8e3f-4c08979f8d12 | AI_MW_T_H_HW_AMEV1 | Sensor Temperature Hot water | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Temperature Reading | {f,f,f,f} | 0 | 0 | {f} | °C |  |  |  | 1.5 | 1 | 300 | [10] | [160] | 1.5 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a106 | 0bf4a0f5-bc4d-429b-b275-da552667d731 | AI_MW_T_H_TO_AMEV1 | Sensor Temperature Thermo Oil | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Temperature Reading | {f,f,f,f} | 0 | 0 | {f} | °C |  |  |  | 3 | 1 | 300 | [0] | [300] | 3 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a107 | 0f891ba8-b1fa-4a0c-839b-8835d5cedef6 | AI_MW_T_H_WW_AMEV1 | Sensor Temperature Warm water | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Temperature Reading | {f,f,f,f} | 0 | 0 | {f} | °C |  |  |  | 1 | 60 | 300 | [55] | [75] | 1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a108 | 2aeebe4e-219a-49ac-bfef-32e7c0a4c92a | AI_MW_T_H_AG_AMEV1 | Sensor Temperature Exhaust Gas | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Temperature Reading | {f,f,f,f} | 0 | 0 | {f} | °C |  |  |  | 10 | 1 | 300 | [-20] | [1300] | 10 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a109 | c84dd10b-0288-4196-b919-1e9c9d9bd04f | AI_MW_T_L_RU_AMEV1 | Sensor Temperature Ventilation Room | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Temperature Reading | {f,f,f,f} | 0 | 0 | {f} | °C |  |  |  | 0.5 | 60 | 300 | [5] | [40] | 0.5 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a110 | 6bbad302-e8f7-4a84-b51c-3e87218c052a | AI_MW_T_L_TP_AMEV1 | Sensor Temperature Dew point | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Temperature Reading | {f,f,f,f} | 0 | 0 | {f} | °C |  |  |  | 0.1 | 60 | 300 | [10] | [20] | 0.1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a111 | 89f8d967-9a68-4e06-9ffa-754922f88227 | AI_MW_T_K_NT_AMEV1 | Sensor Temperature Cold Low Temperature | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Temperature Reading | {f,f,f,f} | 0 | 0 | {f} | °C |  |  |  | 0.1 | 60 | 300 | [4] | [14] | 0.1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a112 | 718ad974-af2f-4146-96d6-bea00ea74ada | AI_MW_T_K_HT_AMEV1 | Sensor Temperature Cold High Temperature | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Temperature Reading | {f,f,f,f} | 0 | 0 | {f} | °C |  |  |  | 0.1 | 60 | 300 | [12] | [22] | 0.1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a113 | b3817b71-21f4-4bfe-9a74-a37195f8dc96 | AI_MW_T_K_KW_AMEV1 | Sensor Temperature Cold water | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Temperature Reading | {f,f,f,f} | 0 | 0 | {f} | °C |  |  |  | 0.5 | 60 | 300 | [-20] | [45] | 0.5 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a114 | c2767d39-1a7a-4f31-8158-1065f295e22b | AI_MW_X_L_RU_AMEV1 | Sensor Humidity absolute Room | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Humidity absolute Reading | {f,f,f,f} | 0 | 0 | {f} | g/m³ |  |  |  | 0.1 | 240 | 300 | [4] | [11,5] | 0.1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a115 | bac01cca-6d06-4acf-a53c-aee331c70ada | AI_MW_X_L_AU_AMEV1 | Sensor Humidity absolute Outside | X |  | X | X | 1.1.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Humidity absolute Reading | {f,f,f,f} | 0 | 0 | {f} | g/m³ |  |  |  | 0.1 | [5 empty] | {f,f} | {t,t,t} | Alarm | * | * | *** | {f} |  |  | 1
a116 | 58a3cfc8-1796-4d99-9fa6-78f30119deb1 | AI_MW_M_L_RU_AMEV1 | Sensor Humidity 0-100% RH Room | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Humidity relative Reading | {f,f,f,f} | 0 | 0 | {f} | %r.F. |  |  |  | 3 | 240 | 300 | [30] | [70] | 3 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a117 | 075de54e-3d27-47c5-93d5-d49f53d9a47a | AI_MW_M_L_AU_AMEV1 | Sensor Humidity 0-100% RH Outside | X |  | X | X | 1.1.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Humidity relative Reading | {f,f,f,f} | 0 | 0 | {f} | %r.F. |  |  |  | 3 | [5 empty] | {f,f} | {t,t,t} | Alarm | * | * | *** | {f} |  |  | 1
a118 | d4eb029a-afde-49be-8433-a80e9836e0ff | AI_MW_P_AMEV1 | Sensor Pressure | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Pressure Reading | {f,f,f,f} | 0 | 0 | {f} | Pa |  |  |  | specify | specify | 300 | [specify] | [specify] | [specify] | specify | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a119 | 2fa98944-1523-4d24-b54f-5ad56518f119 | AI_MW_P_GAS_AMEV1 | Sensor Compressed Gas (e.g. natural gas, technical gases) | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Pressure Reading | {f,f,f,f} | 0 | 0 | {f} | bar |  |  |  | specify | specify | 300 | [specify] | [specify] | [specify] | specify | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a120 | a91696d3-f510-49ff-8e26-a74b81b1f383 | AI_MW_P_GM_AMEV1 | Sensors Compressed Gas Hazard (see NC100) | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Pressure Reading | {f,f,f,f} | 0 | 0 | {f} | bar |  |  |  | specify | specify | 100 | [specify] | [specify] | [specify] | specify | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a121 | 5fa7e6c7-9fdc-404e-aa3e-6417d5b9e94c | AI_MW_P_L_AMEV1 | Sensor Pressure 0-1000Pa Ventilation | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Pressure Reading | {f,f,f,f} | 0 | 0 | {f} | Pa |  |  |  | [30] | 120 | 300 | [0] | [500] | [30] | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a122 | 063cbe52-fcf7-4c05-8ac5-c61e10a26ef1 | AI_MW_P_Tem_AMEV1 | Sensor Pressure 0-10bar heating | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Pressure Reading | {f,f,f,f} | 0 | 0 | {f} | bar |  |  |  | 0.1 | 30 | 300 | [1,5] | [5] | 0.1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a123 | d4a75ac9-4226-4ca5-a049-5c6b1a48ca19 | AI_MW_PD_L_AMEV1 | Sensor Differential Pressure 0-5000/(+-50 ring scale)Pa differential pressure ventilation | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Pressure difference Reading | {f,f,f,f} | 0 | 0 | {f} | Pa |  |  |  | [150/3] | 120 | 300 | [0/-40] | [500/40] | [150/3] | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1/120
a124 | b482754f-25a2-4a8a-ad5d-65d5ffeed0fc | AI_MW_PD_Tem_AMEV1 | Sensor Differential Pressure 0-5.5bar differential pressure heating | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Pressure difference Reading | {f,f,f,f} | 0 | 0 | {f} | bar |  |  |  | 0.1 | 30 | 300 | [1,5] | [5] | 0.1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a125 | 3f1625fa-e598-4fa7-982b-377758f2c97a | AI_MW_F_AMEV1 | Sensor Volume Flow Counter, Volume Flow Controller | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Volume flow Measured value | {f,f,f,f} | 0 | 0 | {f} | m3/h |  |  |  | specify | specify | 300 | [specify] | [specify] |  | specify | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a126 | 1b7596c2-69b1-4383-ab31-f892b6a661be | AI_MW_J_AMEV1 | Sensor Power Counter | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Performance Metric | {f,f,f,f} | 0 | 0 | {f} | kW |  |  |  | specify | specify | 300 | [specify] | [specify] |  | specify | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a127 | 862891c7-7141-40fa-aec2-a39790b15134 | AI_MW_QCD_AMEV1 | Sensor CO2 Carbon dioxide | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | CO2 Reading | {f,f,f,f} | 0 | 0 | {f} | ppm |  |  |  | 50 | 3600 | 300 | [400] | [1200] | 50 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a128 | 53735a65-bd13-4a65-be6d-9d62908c3222 | AI_MW_QCO_AMEV1 | Sensor CO Carbon monoxide | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | CO Reading | {f,f,f,f} | 0 | 0 | {f} | ppm |  |  |  | [1] | 3600 | 200 | [0] | [30] | 1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a129 | c74b246d-5eaf-45cd-92c7-f6807bb391e1 | AI_MW_QPH_AMEV1 | Sensor Conductivity | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | PH Reading | {f,f,f,f} | 0 | 0 | {f} | pH |  |  |  | [0,1] | 3600 | 300 | [6] | [8] | [0,1] | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a130 | d9d0c12a-b62a-4162-8a40-fd93b517bbb9 | AI_MW_E_RU_AMEV1 | Sensor Illuminance Room | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Illuminance Reading | {f,f,f,f} | 0 | 0 | {f} | lx |  |  |  | 50 | 3600 | 300 | 0 | [1000] | 50 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a131 | f46a9485-9ca6-4280-8f39-afd9551ad445 | AI_MW_E_AU_AMEV1 | Sensor Illuminance Outside | X |  | X | X | 1.1.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Illuminance Reading | {f,f,f,f} | 0 | 0 | {f} | lx |  |  |  | 50 | 3600 | 300 |  |  |  | {f,f} | {f,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a132 | d8968258-1895-4231-8956-6738f46688c4 | AI_MW_R_AU_AMEV1 | Sensor Global Radiation Outside | X |  | X | X | 1.1.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Global radiation Reading | {f,f,f,f} | 0 | 0 | {f} | W/m² |  |  |  | 50 | 3600 | 300 |  |  |  | {f,f} | {f,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a133 | ef55d7b8-8592-4705-8401-774c060d4164 | AI_MW_L_AMEV1 | Sensor Level | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Level Reading | {f,f,f,f} | 0 | 0 | {f} | [%] |  |  |  | [0,5] | 3600 | 300 | [20] | [100] | [1] | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a134 | 0f3b5b89-35fb-4100-b47d-2678f1a01963 | AI_RW_AMEV1 | Feedbacxk value | X |  | X | X | 1.1.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Feedbacxk value | {f,f,f,f} | 0 | 0 | {f} | % |  |  |  | 3 | 60 | 300 | [0] | [100] | 3 | {f,f} | {f,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a135 | 894896d3-a42d-46ae-88ac-d1f9ab231be2 | AI_MW_WIG_AMEV1 | Sensor: Thermal Anemometer/Star Anemometer | X |  | X | X | 1.1.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Wind speed Reading | {f,f,f,f} | 0 | 0 | {f} | m/s |  |  |  | 0.1 | 60 | 300 |  |  |  | {f,f} | {f,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a136 | 32295474-6ba0-497e-8121-d779093ab883 | AI_MW_RW_AMEV1 | Performance feedback | X |  | X | X | 1.1.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Performance Feedback | {f,f,f,f} | 0 | 0 | {f} | % |  |  |  | 3 | 60 | 300 | [0] | [100] | 3 | {f,f} | {f,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a137 | 14a47d97-ef24-4ff2-a394-e0047149b373 | AI_MW_LTF_AMEV1 | Conductivity | X |  | X | X | 1.1.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Conductivity Measured Value | {f,f,f,f} | 0 | 0 | {f} | S/m |  |  |  | [0,1] | 60 | 300 |  |  |  | {f,f} | {f,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a138 | bd849768-c7e4-4d4c-8a99-ab5942a2bfb2 | AI_SW_J_AMEV1 | Setpoint Power (feed-in) | X | X | X | X | 1.1.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Power Setpoint | {f,f,f,f} | 0 | 0 | {f} | % |  |  |  | specify | specify | 300 | [specify] | [specify] |  | specify | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
|  | * B (Builder/Operator), P (Planning), X (Executing Company) | [6 empty] | Default value (parameterization) and test value | [10 empty] | [] => Default value (suggestion) | [8 empty] | * Can be used for testing in the 1:1 test
[9 empty] | Test value (internally generated value) | [19 empty] | *** Implementation according to Chapter 4.5

## 8.2 AO_AV
ObjSort + LfdNr | UUID | Objekt-Template- Kennung | Kommentar | GA-FL Einträge (1.1.3) | GA-FL Einträge (1.2.1) | GA-FL Einträge (2.2.1) | GA-FL Einträge (2.2.2) | GA-FL Einträge (2.2.3) | GA-FL Einträge (3.1.1) | GA-FL Einträge (3.1.3) | GA-FL Einträge (Abschnitte/Spalten) | Object_Name | Description | Verwendung | Status_Flags | Event_State | Reliability | Out_Of_Service | Units | Min_Pres_Value | Max_Pres_Value | Resolution | Relinquish_Default | COV_Increment | Time_Delay | Notification_Class | Low_Limit | High_Limit | Deadband | Limit_Enable | Event_Enable | Notify_Type | Event_Time_Stamps | Event_Message_Texts | Event_Message_Texts_Config | Event_Detection_Enable | Event_Algorithm_Inhibit | Event_Algorithm_Inhibit_Ref | Time_Delay_Normal | Reliability_Evaluation_Inhibit | Current_Command_Priority | Letztmalige Änderung in Version
|  | PropSort | [9 empty] | a11 | a12 | [5 empty] | b11 | c45 | c46 | b41 | b16 | b17 | c43 | c11 | c47 | c48 | c50 | c49 | c12 | c13 |  |  | c14 | c15 | c41 | c42 | c44
|  | Conformance Code | [9 empty] | R | W |  | R | R | W1 | W | W | R | R | R | W | W | W | W | W | W | W | W | W | W | R | R | W | W | RA | RA | W | RX¦O | R22
|  | Grundlegende Vorgabe * | [9 empty] | B * | B | [5 empty] | B | P | P | P | B | B | P | B | P | P | P | P | B | B |  |  | B | B | P | P | P
|  | Detailierte Festlegung * | [9 empty] | P * | P | [5 empty] | P | P | P | P | P | P | P | P | P | P | P | P | P | P |  |  | P | P | P | P | P
|  | Umsetzung * | [9 empty] | X * | U |  | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U |  |  | U | U | U | U | U | U | U
|  | Vorgabewert (Parametrierung) | [9 empty] | ja | ja |  | nein | nein | nein | nein | ja | ja | ja | nein | ja | ja | ja | ja | ja | ja | ja | ja | ja | ja | nein | nein | ja | ja | nein | nein | ja | nein | nein
a201 | b6b83fde-bb6c-4e8f-9b10-7ad4203a2c15 | AO_ST_AMEV1 | 0-10V/4-20mA | X |  |  |  |  | X | X | 1.1.3; 3.1.1; 3.1.3 | [BAS] | [Description] | Stellsignal | {f,f,f,f} | 0 | 0 | {f} | % | 0 | 100 |  |  | 2.5 | [11 empty] | {f} |  |  |  |  | >8
a202 | 38bc28d4-c13c-4a50-b514-2f75996dd08b | AO_SW_T_AMEV1 | 0-10V/4-20mA | X |  |  |  |  | X | X | 1.1.3; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Temperatur (Hardwareaufschaltung) | {f,f,f,f} | 0 | 0 | {f} | °C | [0] | [50] |  |  | 0.5 | [11 empty] | {f} |  |  |  |  | >8
a203 | f2fb7788-7569-4c9e-bad7-9776d90ea72d | AO_SWC_T_AMEV1 | 0-10V/4-20mA | X |  |  |  |  | X | X | 1.1.3; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Temperatur berechnet (Hardwareaufschaltung) | {f,f,f,f} | 0 | 0 | {f} | °C | [0] | [50] |  |  | 0.5 | [11 empty] | {f} |  |  |  |  | >8
a204 | 602ac6eb-b36d-443f-891c-3337f04fc162 | AO_SW_F_AMEV1 | 0-10V/4-20mA | X |  |  |  |  | X | X | 1.1.3; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Volumenstrom | {f,f,f,f} | 0 | 0 | {f} | m³/h |  |  |  | festlegen | >0 | [11 empty] | {f}
a205 | 6dc8473a-8b77-44a4-b339-84b687ae6bb2 | AO_SW_PD_AMEV1 | 0-10V/4-20mA | X |  |  |  |  | X | X | 1.1.3; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Förderhöhe | {f,f,f,f} | 0 | 0 | {f} | m | [0] | [10] |  |  | 0.2 | [11 empty] | {f} |  |  |  |  | >8
a206 | 22995b24-b076-41f8-be55-17ede4d38b36 | AO_MWC_J_AMEV1 | 0-10V/4-20mA | X |  |  |  |  | X | X | 1.1.3; 3.1.1; 3.1.3 | [BAS] | [Description] | Messwert Leistung berechnet (Energieeinspeisung) | {f,f,f,f} | 0 | 0 | {f} | % | 0 | 100 |  |  | 2.5 | [11 empty] | {f} |  |  |  |  | >8
a301 | fa350b5d-0aaa-4789-824c-86a0f145ce3c | AV_ST_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Stellsignal | {f,f,f,f} | 0 | 0 | {f} | % | 0 | 100 |  |  | 2.5 | [11 empty] | {f} |  |  |  |  | >8
a302 | a77a1e27-eba8-4e83-b913-a73745467cc8 | AV_RW_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Rückführwert | {f,f,f,f} | 0 | 0 | {f} | % | 0 | 100 |  |  | 2.5 | [11 empty] | {f} |  |  |  |  | >8
a303 | 5e0c8196-ffac-4211-9a85-7c796cd52da1 | AV_SW_T_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Temperatur | {f,f,f,f} | 0 | 0 | [5 empty] | festlegen | >0 | 1 | 500 | festlegen | festlegen | 0.5 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a304 | a07256bd-b829-4aac-83be-0c0f069eed1b | AV_SW_TH_RU_S_AMEV1 | P<E |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Temperatur Heizen Protection (Schutzbetrieb) | {f,f,f,f} | 0 | 0 |  | °C | 5 | 15 |  | 6 | 0.1 | 1 | 500 | 5 | 15 | 0.5 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a305 | cd54f20f-b585-4aca-a7a9-03e98eaf4aed | AV_SW_TH_RU_E_AMEV1 | E<PK |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Temperatur Heizen Economy (Absenkbetrieb) | {f,f,f,f} | 0 | 0 |  | K | [-10] | [-6] |  | [-8] | 0.1 | 1 | 500 | [-10] | [-6] | 0.1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a306 | 9333b7ce-66ff-40c0-811c-f8f956c1f2b9 | AV_SW_TH_RU_P_AMEV1 | PK<K |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Temperatur Heizen Pre-Komfort (Abwesend) | {f,f,f,f} | 0 | 0 |  | K | [-6] | [-4] |  | [-4] | 0.1 | 1 | 500 | [-6] | [-4] | 0.1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a307 | 929e22e8-9367-4dba-87cd-f787f05426ad | AV_SW_TH_RU_K_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Temperatur Heizen Komfort | {f,f,f,f} | 0 | 0 |  | K | [-4] | [0] |  | [-2] | 0.1 | 1 | 500 | [-4] | [0] | 0.1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a308 | ec9a4ea9-8bfe-48c6-8e5d-bc9cfe7116c1 | AV_SW_T_RU_B_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Temperatur Basis | {f,f,f,f} | 0 | 0 |  | °C | [20] | [24] |  | [22] | 0.1 | 1 | 500 | [20] | [24] | 0.1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a309 | 8add1bac-b43d-4e41-8c02-c8432d10f033 | AV_SW_T_RU_V_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Temperatur Verstellung | {f,f,f,f} | 0 | 0 |  | °C | [-3] | [3] |  | [0] | [12 empty] | {t} |  |  | 1 |  | >8 | AMEV1.1
a310 | 1c61a6fe-db6f-4657-bbdb-afeeb813a768 | AV_SW_TK_RU_K_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Temperatur Kühlen Komfort | {f,f,f,f} | 0 | 0 |  | K | [2] | [4] |  | [+2] | 0.1 | 1 | 500 | [2] | [4] | 0.1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a311 | 0d44739c-5798-4e35-8819-2adfb9396a5e | AV_SW_TK_RU_P_AMEV1 | PK>K |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Temperatur Kühlen Pre-Komfort | {f,f,f,f} | 0 | 0 |  | K | [4] | [6] |  | [+4] | 0.1 | 1 | 500 | [4] | [6] | 0.1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a312 | dd7b5a4f-1803-4aaa-93f7-4b3f8e31d1a5 | AV_SW_TK_RU_E_AMEV1 | E>PK |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Temperatur Kühlen Economy | {f,f,f,f} | 0 | 0 |  | K | [6] | [10] |  | [+8] | 0.1 | 1 | 500 | [6] | [10] | 0.1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a313 | 004c44a7-6eec-471c-a17a-aac79d275fb5 | AV_SW_TK_RU_S_AMEV1 | P>E |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Temperatur Kühlen Protection | {f,f,f,f} | 0 | 0 |  | °C |  |  |  | 40 | 0.1 | 1 | 500 | 40 | 42 | 0.5 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a314 | 6aea1451-12f9-4b84-bcaa-4fbb0f7f2c6e | AV_SW_T_RU_V_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Temperatur Versteller | {f,f,f,f} | 0 | 0 |  | K | [-3] | [3] |  | [0] | 0.5 | 1 | 500 | [-3] | [3] | 0.5 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a315 | a8e3bea2-da65-4939-ac73-f9fa37578602 | AV_SWC_TH_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Temperatur Heizen berechnet | {f,f,f,f} | 0 | 0 | {f} | °C |  |  |  |  | 0.5 | [11 empty] | {f} |  |  | 1 |  | >8
a316 | 2ae99910-a66d-45f7-86a8-018596801445 | AV_SWC_TK_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Temperatur Kühlen berechnet | {f,f,f,f} | 0 | 0 | {f} | °C |  |  |  |  | 0.5 | [11 empty] | {f} |  |  | 1 |  | >8
a317 | 4af8731c-8fd0-4d9d-b288-1700a5054516 | AV_SW_M_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Feuchte | {f,f,f,f} | 0 | 0 |  | %rF |  |  |  | festlegen | 0.5 | 1 | 500 | festlegen | festlegen | 2 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a318 | c20790af-4a0f-4c99-afdd-4892877395ae | AV_SW_ME_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Feuchte Entfeuchten | {f,f,f,f} | 0 | 0 |  | %rF |  |  |  | 65% | 0.5 | 1 | 500 | [60] | [70] | 2 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a319 | 89bb90cf-2e59-4d2d-aa5f-8d1f453094a9 | AV_SW_MB_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Feuchte Befeuchten | {f,f,f,f} | 0 | 0 |  | %rF |  |  |  | 30% | 0.5 | 1 | 500 | [25] | [35] | 2 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a320 | 91ecbf73-3f95-4456-aec3-9a79bafa14b9 | AV_SWC_X_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Feuchte berechnet | {f,f,f,f} | 0 | 0 | {f} | g/kg |  |  |  |  | 0.1 | [11 empty] | {f} |  |  | 1 |  | >8
a321 | 868cbb23-9ab8-4def-b3a8-cdb90c924079 | AV_SWC_XE_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Feuchte Entfeuchten berechnet | {f,f,f,f} | 0 | 0 | {f} | g/kg |  |  |  |  | 0.1 | [11 empty] | {f} |  |  | 1 |  | >8
a322 | a4df2f83-f6ea-4ca5-a3a2-e7eb0d3b2a9e | AV_SWC_XB_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Feuchte Befeuchten berechnet | {f,f,f,f} | 0 | 0 | {f} | g/kg |  |  |  |  | 0.1 | [11 empty] | {f} |  |  | 1 |  | >8
a323 | 6a6ebd18-5a1b-4de1-abdc-386f8cd41449 | AV_SW_P_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Druck | {f,f,f,f} | 0 | 0 | [6 empty] | festlegen | festlegen | 300 | festlegen | festlegen | festlegen | festlegen | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a324 | 1232b805-69b4-4e01-b98a-d23a414281fb | AV_SW_P_L_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Druck | {f,f,f,f} | 0 | 0 |  | Pa |  |  |  |  | [30] | 120 | 300 | [0] | [500] | [30] | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a325 | 45e86ba4-2889-4a4f-a107-6b2c8c65686b | AV_SW_P_H_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Druck | {f,f,f,f} | 0 | 0 |  | bar |  |  |  |  | 0.1 | 30 | 300 | [1,5] | [5] | 0.1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a326 | 139663c0-7552-4238-9d7a-94d3ea8f9c28 | AV_SW_PD_L_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Druck Differenz | {f,f,f,f} | 0 | 0 |  | Pa |  |  |  |  | [150/3] | 120 | 300 | [0/-40] | [500/40] | [150/3] | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a327 | e45c1a2e-d734-4b23-807a-e896c9cc2267 | AV_SW_PD_H_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Druck Differenz | {f,f,f,f} | 0 | 0 |  | bar |  |  |  |  | 0.1 | 30 | 300 | [1,5] | [5] | 0.1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a328 | 793af15c-dddd-4c81-8394-4d2a1415956e | AV_SW_F_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Volumenstrom | {f,f,f,f} | 0 | 0 |  | m³/h |  |  |  | festlegen | >0 | 1 | 500 | festlegen | festlegen | [10] | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a329 | 3b7086b0-42ec-4606-a22b-6fdb3c130802 | AV_SW_QCD_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Luftqualität CO2 | {f,f,f,f} | 0 | 0 |  | ppm |  |  |  |  | [10] | 1 | 300 | [800] | [1200] | [10] | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a330 | 2c975540-bd4e-4e87-b944-3e693d0bccd1 | AV_SW_Q_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Luftqualität IAQ (indoor air quality) | {f,f,f,f} | 0 | 0 |  | % |  |  |  |  | [1] | 1 | 300 |  | [50] | [1] | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a331 | 5e67c035-148f-4d90-96ba-3cfe6ac0f19d | AV_SW_QVO_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Luftqualität VOC | {f,f,f,f} | 0 | 0 |  | % |  |  |  |  | [1] | 1 | 300 |  | [50] | [1] | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a332 | 9b95296c-90f7-430d-b726-0d1f5b52cc81 | AV_SW_25QPF_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Luftqualität Feinstaub 2,5 | {f,f,f,f} | 0 | 0 |  | µg/m³ |  |  |  |  | [1] | 1 | 300 |  | [25] | [1] | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a333 | 6574e262-8e08-4770-80a6-2fdba2fc5164 | AV_SW_10QPF_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Luftqualität Feinstaub 10 | {f,f,f,f} | 0 | 0 |  | µg/m³ |  |  |  |  | [1] | 1 | 300 |  | [50] | [1] | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a334 | ef0e547c-75f2-49e7-8708-2e819ed0f1bb | AV_ST_E_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Beleuchtung | {f,f,f,f} | 0 | 0 |  | % |  |  |  |  | [2,5] | [11 empty] | {t} |  |  | 1 |  | >8
a335 | 29a66529-29f2-4be7-9206-c7298598b394 | AV_ST_ER_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Beleuchtung reduziert | {f,f,f,f} | 0 | 0 |  | % |  |  |  |  | [2,5] | [11 empty] | {t} |  |  | 1 |  | >8
a336 | 4df92393-fbf8-43aa-bcb0-ddd262ec2725 | AV_SW_E_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Beleuchtungsstärke | {f,f,f,f} | 0 | 0 |  | lux |  |  |  |  | [25] | 1 | 300 | [100] | [600] | [10] | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a337 | f40af017-2287-4357-a384-cb9fbc446589 | AV_SW_ER_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Beleuchtungsstärke reduziert | {f,f,f,f} | 0 | 0 |  | lux |  |  |  |  | [25] | [11 empty] | {t} |  |  | 1 |  | >8
a338 | 1e727c70-3064-44de-b73d-dbf3c06ea6b8 | AV_SW_POS_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Position | {f,f,f,f} | 0 | 0 |  | % |  |  |  |  | [2,5] | [11 empty] | {t} |  |  | 1 |  | >8
a339 | 02564efb-00ce-4ec3-b4ae-ae99d8227ced | AV_SW_WIN_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sollwert Winkel | {f,f,f,f} | 0 | 0 |  | ° |  |  |  |  | [5] | [11 empty] | {t} |  |  | 1 |  | >8
a340 | 65dbd921-1604-4eba-b6e1-237904a3a5f7 | AV_ST_POS_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Stellsignal Position | {f,f,f,f} | 0 | 0 |  | % |  |  |  |  | [2,5] | [11 empty] | {t} |  |  | 1 |  | >8
a341 | 59183b39-faf2-469e-a532-02ff3f635ff6 | AV_ST_WIN_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Stellsignal Winkel | {f,f,f,f} | 0 | 0 |  | ° |  |  |  |  | [5] | [11 empty] | {t} |  |  | 1 |  | >8
a342 | 37977761-1d25-45e8-bb09-44f83db4c80a | AV_MW_T_AMEV1 | kommunikativ |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Messwert Temperatur | {f,f,f,f} | 0 | 0 | {f} | °C |  |  |  | 0 | 0.5 | 60 | 300 | [5] | [40] | 0.5 | {t,t} | {t,t,t} | Alarm | * | * | *** | {f} |  |  |  |  | >8
a343 | 454cac39-0911-4a47-9298-352c8a72cb41 | AV_MW_T_AU_AMEV1 | kommunikativ, Außen |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Messwert Temperatur | {f,f,f,f} | 0 | 0 | {f} | °C |  |  |  | 0 | 0.2 | [11 empty] | {f} |  |  |  |  | >8
a344 | eafc4935-10ac-422f-8252-b9045ed3bd6e | AV_MWC_TD_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Messwert berechnet Temperaturdifferenz | {f,f,f,f} | 0 | 0 | {f} | K |  |  |  | 0 | [0,2] | [11 empty] | {f} |  |  |  |  | >8
a345 | bb187aab-9b02-4c62-a7c2-3b7880e174ff | AV_MW_M_AU_AMEV1 | kommunikativ, Außen |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | relative Feuchte Messwert | {f,f,f,f} | 0 | 0 | {f} | %r.F. |  |  |  | 0 | 3 | [11 empty] | {f} |  |  |  |  | >8
a346 | 0e6b1f8a-fa03-48f2-9452-3b471aca1997 | AV_MW_F_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Volumenstrom Messwert | {f,f,f,f} | 0 | 0 | {f} | m³/h |  |  |  | 0 | [25] | [11 empty] | {f} |  |  |  |  | >8
a347 | e70cb5db-3f4f-4f91-b3f0-0301e876a36b | AV_MW_DMZ_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Volumenstrom Dampf Messwert | {f,f,f,f} | 0 | 0 | {f} | [to/h]* |  |  |  | 0 | [1] | [11 empty] | {f} |  |  |  |  | >8
a348 | 8ea8ea92-3202-406e-82f5-3fe49af2e05d | AV_ZW_F_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Menge Messwert | {f,f,f,f} | 0 | 0 | {f} | m³ |  |  |  | 0 | [1] | [11 empty] | {f} |  |  |  |  | >8
a349 | 2fbefa74-9ddb-4aaa-9778-f2cf59477eec | AV_MWC_GTZ_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Gradtagszahl Messwert berechnet | {f,f,f,f} | 0 | 0 | {f} | Kd |  |  |  | 0 | 0.1 | [11 empty] | {f} |  |  |  |  | >8
a350 | f1ec52c1-c161-476c-88e2-33e6d84d3baa | AV_MWC_WG_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Wirkungsgrad (COP) Messwert berechnet | {f,f,f,f} | 0 | 0 | {f} |  |  |  |  | 0 | 0.1 | [11 empty] | {f} |  |  |  |  | >8
a351 | efa41d69-1f94-47f4-aa91-d7fc27d66e99 | AV_MWC_RWZ_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Rückwärmezahl Messwert berechnet | {f,f,f,f} | 0 | 0 | {f} |  |  |  |  | 0 | [2,5] | 900 | 300 | [73] |  | 1 | {t,f} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a352 | 7ea94aff-14df-47ce-b111-aa2df1cef9ac | AV_MW_WIG_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Windgeschwindigkeit Messwert | {f,f,f,f} | 0 | 0 | {f} | m/s |  |  |  | 0 | [2,5] | [11 empty] | {f} |  |  |  |  | >8
a353 | 7e5f7adf-6742-4309-b63b-d739abfeef69 | AV_MWC_WIG_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Windgeschwindigkeit Messwert berechnet | {f,f,f,f} | 0 | 0 | {f} | m/s |  |  |  | 0 | [2,5] | [11 empty] | {f} |  |  |  |  | >8 | AMEV1.1
a354 | 51d19626-6a73-480d-a79c-9598a3337b93 | AV_MW_WIR_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Windrichtung/Sonnenstand Messwert | {f,f,f,f} | 0 | 0 | {f} | ° |  |  |  | 0 | [5] | [11 empty] | {f} |  |  |  |  | >8
a355 | cde95bc7-817f-4a8a-a62b-f8d431d47af8 | AV_MWC_WIR_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Windrichtung Messwert berechnet | {f,f,f,f} | 0 | 0 | {f} | ° | 0 | 360 |  | 0 | [5] | [11 empty] | {f} |  |  |  |  | >8 | AMEV1.1
a356 | f26f9f12-0f15-4480-9cea-60d64938b96f | AV_MW_E_RU_AMEV1 | kommunikativ, Raum |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Beleuchtungsstärke Messwert | {f,f,f,f} | 0 | 0 | {f} | lx |  |  |  | 0 | 50 | [11 empty] | {f} |  |  |  |  | >8
a357 | d0a64df9-ce90-4221-8262-464aa81f7dde | AV_MW_E_AU_AMEV1 | kommunikativ, Außen |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Beleuchtungsstärke Messwert | {f,f,f,f} | 0 | 0 | {f} | klx |  |  |  | 0 | [5] | [11 empty] | {f} |  |  |  |  | >8
a358 | e863528b-f406-4304-b75c-74943af8e925 | AV_MW_R_AU_AMEV1 | kommunikativ, Außen |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Globalstrahlung Messwert | {f,f,f,f} | 0 | 0 | {f} | W/m² |  |  |  | 0 | [5] | [11 empty] | {f} |  |  |  |  | >8
a359 | 1a061bfb-2284-45a1-8e20-c3c63b8e88a0 | AV_MW_ALxN_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Spannung Messwert | {f,f,f,f} | 0 | 0 | {f} | V |  |  |  | 0 | 5 | 5 | 300 | [207] | [253] | 1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 0 |  | >8
a360 | beabcea7-b85e-4d95-8bca-296011e0baeb | AV_MW_C_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Strom Messwert | {f,f,f,f} | 0 | 0 | {f} | A |  |  |  | 0 | [] | [60] | 300 | 0 | [] | [] | {f,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 0 |  | >8
a361 | 715dd801-b490-4ebf-b63f-96cc5079318a | AV_MW_S_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Frequenz Messwert | {f,f,f,f} | 0 | 0 | {f} | Hz |  |  |  | 0 | 0.1 | 5 | 300 | [47,5] | [52,5] | 0.1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 0 |  | >8
a362 | 4b4683ec-ae63-4cf5-acc9-0f96fdf87a51 | AV_MW_J_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Wirkleistung Messwert | {f,f,f,f} | 0 | 0 | {f} | [kW]* |  |  |  | 0 | [] | [60] | 300 | 0 | [] | [] | {f,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 0 |  | >8
a363 | 30ae53c1-68d3-4c83-a640-ef0832210737 | AV_MW_COS_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Leistungsfaktor Messwert | {f,f,f,f} | 0 | 0 | {f} |  |  |  |  | 0 | 0.05 | [60] | 300 | [0,8] | [1] | 0.1 | {t,f} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 0 |  | >8
a364 | c8a41c6b-8c08-4127-80f5-70df11367e39 | AV_MW_POS_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Position Messwert | {f,f,f,f} | 0 | 0 | {f} | % |  |  |  | 0 | [2,5] | [11 empty] | {f} |  |  |  |  | >8
a365 | a0e46371-7f8f-4a23-8ab7-88f602602ccc | AV_MW_WIN_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Winkel Messwert | {f,f,f,f} | 0 | 0 | {f} | ° |  |  |  | 0 | [5] | [11 empty] | {f} |  |  |  |  | >8
a366 | 6460d920-6032-4a7e-ba79-41c23695176e | AV_MWC_POS_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Position berechnet Messwert berechnet | {f,f,f,f} | 0 | 0 | {f} | % |  |  |  | 0 | [2,5] | [11 empty] | {f} |  |  |  |  | >8
a367 | 47943f97-31c0-4645-84da-68795893a8b2 | AV_MWC_WIN_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Winkel berechnet Messwert berechnet | {f,f,f,f} | 0 | 0 | {f} | ° |  |  |  | 0 | [5] | [11 empty] | {f} |  |  |  |  | >8
a368 | 132383a3-20b1-484a-a6ce-866088c69ed6 | AV_ZAF_LAM_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Lastmessung Kabine Messwert | {f,f,f,f} | 0 | 0 | {f} | kg | 0 | [630] |  | 0 | 75 | 1 | 800 | 0 | [630] | 1 | {f,t} | {t,t,t} | Event | * | * |  | {t} |  |  | 1 |  | >8
a369 | dfb6d6c5-4572-4374-b137-6160157e97dd | AV_ZAF_S_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Geschwindigkeit Kabine Messwert | {f,f,f,f} | 0 | 0 | {f} | m/s | 0 | [20] |  | 0 | [0,5] | [11 empty] | {f} |  |  |  |  | >8
a370 | 2ca4fefe-d5ff-4b11-910b-c241d643a32d | AV_ZAF_ABW_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Abweichung Anhaltegenauigkeit Messwert | {f,f,f,f} | 0 | 0 | {f} | mm | [-150] | [150] |  | 0 | 1 | 1 | 300 | -10 | 10 | 1 | {f,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a371 | fcc58365-338e-4d0b-a570-81d3c03ef487 | AV_PAR_F_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Volumenstrom Parameter | {f,f,f,f} | 0 | 0 | {f} | m³/h | 0 |  |  | [VVR min] | [5] | [11 empty] | {f} |  |  |  |  | >8
a372 | 7b4e7de2-30d3-42bd-804c-80da2ee5bd95 | AV_PAR_K_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Zeit Parameter | {f,f,f,f} | 0 | 0 | {f} | s | 0 |  |  |  | 1 | [11 empty] | {f} |  |  |  |  | >8
a373 | 37237666-54c9-4278-ad23-3518324f6224 | AV_PAR_NL_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Nachlaufzeit Parameter | {f,f,f,f} | 0 | 0 | {f} | s |  |  |  | festlegen | 1 | [11 empty] | {f} |  |  |  |  | >8
a374 | 8413e24b-e7a1-48e4-ad05-cc2518c4aa9d | AV_PAR_OHZ_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Offenhaltezeit Parameter | {f,f,f,f} | 0 | 0 | {f} | s |  |  |  | festlegen | 1 | [11 empty] | {f} |  |  |  |  | >8
a375 | 7179fff3-3551-4c25-9dac-7d8edd67ba0e | AV_ZW_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Zählwert | {f,f,f,f} | 0 | 0 | {f} |  |  |  |  | 0 | [1] | [11 empty] | {f} |  |  |  |  | >8
a376 | 4d2ec8e3-f5ab-47f3-aafd-993674663080 | AV_ZW_H_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Zählwert Verbrauch (oder Bezug/Erzeugung) | {f,f,f,f} | 0 | 0 | {f} | [kWh]* |  |  |  | 0 | [1] | [5 empty] | {f,f} | {f,t,t} | Alarm | * | * | *** | {t} |  |  | 0 |  | >8
a377 | 3ec64193-c816-4868-a631-5b055ae266da | AV_ZW_HVR_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Zählwert Blindarbeit | {f,f,f,f} | 0 | 0 | {f} | [kvarh]* |  |  |  | 0 | [1] | [5 empty] | {f,f} | {f,t,t} | Alarm | * | * | *** | {t} |  |  | 0 |  | >8
a378 | 1b33c9ff-7db7-4f70-8180-b2eca61993a4 | AV_ZW_DMZ_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Zählwert Verbrauch (oder Bezug/Erzeugung) | {f,f,f,f} | 0 | 0 | {f} | [to]* |  |  |  | 0 | [1] | [5 empty] | {f,f} | {f,t,t} | Alarm | * | * | *** | {t} |  |  | 0 |  | >8
a379 | 28c57476-d9cf-4886-8dab-1b783ff9357e | AV_MWC_ZFA_AMEV1 |  |  | X |  |  | X | X | X | 1.2.1; 2.2.3; 3.1.1; 3.1.3 | [BAS] | [Description] | Zähler Fahrten / Offnungen | {f,f,f,f} | 0 | 0 | {f} |  | 0 |  |  | 0 | [1] |  | 400 |  | [] | 1 | {f,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a380 | 34396254-f208-438c-99bd-7c96ba15e91b | AV_SN_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Seriennummer | {f,f,f,f} | 0 | 0 | {f} |  |  |  |  | aktuelle SN | 1 | 0 | 420 | aktuelle SN | aktuelle SN |  | {f,f} | {f,t,t} | Alarm | * | * | *** | {t} |  |  | 0 |  | >8
a381 | 133198ef-0c03-46d1-a6b7-5b309547ffc8 | AV_MWC_BZ_AMEV1 |  |  | X |  | X |  | X | X | 1.2.1;2.2.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Betriebsstunden | {f,f,f,f} | 0 | 0 | {f} | h | 0 |  |  | 0 | 1 | 1 | 400 | 0 | [8760] | 1 | {f,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
|  | * B (Bauherr/Betreiber), P (GA-Planung), U (Ausführendes Unternehmen) | [9 empty] | Vorgabewert (Parametrierung) und Prüfwert | [6 empty] | [] => Default-Werte (Vorschlag) | [13 empty] | *Kann zur Prüfung des 1:1 Test herangezogen werden
[12 empty] | Prüfwert (im System erzeugter Wert) | [6 empty] | * Einheiten von Zählern sollen im Projekt einheitlich sein | [13 empty] | *** gemäß Kapitel 4.4 einrichten
ENGLISH VERSION (Draft)
ObjSort + No. | UUID | Object Template Identifier | Comment | BACS FL entries (1.1.3) | BACS FL entries (1.2.1) | BACS FL entries (2.2.1) | BACS FL entries (2.2.3) | BACS FL entries (2.2.3) | BACS FL entries (3.1.1) | BACS FL entries (3.1.3) | BACS FL entries (sections/columns) | Object_Name | Description | Application | Status_Flags | Event_State | Reliability | Out_Of_Service | Units | Min_Pres_Value | Max_Pres_Value | Resolution | Relinquish_Default | COV_Increment | Time_Delay | Notification_Class | Low_Limit | High_Limit | Deadband | Limit_Enable | Event_Enable | Notify_Type | Event_Time_Stamps | Event_Message_Texts | Event_Message_Texts_Config | Event_Detection_Enable | Event_Algorithm_Inhibit | Event_Algorithm_Inhibit_Ref | Time_Delay_Normal | Reliability_Evaluation_Inhibit | Current_Command_Priority | Last change in version
|  | PropSort | [9 empty] | a11 | a12 | [5 empty] | b11 | c45 | c46 | b41 | b16 | b17 | c43 | c11 | c47 | c48 | c50 | c49 | c12 | c13 |  |  | c14 | c15 | c41 | c42 | c44
|  | Conformance Code | [9 empty] | R | W |  | R | R | W1 | W | W | R | R | R | W | W | W | W | W | W | W | W | W | W | R | R | W | W | RA | RA | W | RX¦O | R22
|  | Basic spezification * | [9 empty] | B * | B | [5 empty] | B | P | P | P | B | B | P | B | P | P | P | P | B | B |  |  | B | B | P | P | P
|  | Detailed definition * | [9 empty] | P * | P | [5 empty] | P | P | P | P | P | P | P | P | P | P | P | P | P | P |  |  | P | P | P | P | P
|  | Implementation * | [9 empty] | X * | X |  | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X |  |  | X | X | X | X | X | X | X
|  | Default value (parameterization) | [9 empty] | yes | yes |  | no | no | no | no | yes | yes | yes | no | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | no | no | yes | yes | no | no | yes | no | no
a201 | b6b83fde-bb6c-4e8f-9b10-7ad4203a2c15 | AO_ST_AMEV1 | 0-10V/4-20mA | X |  |  |  |  | X | X | 1.1.3; 3.1.1; 3.1.3 | [UAK] | [Description] | Setting signal | {f,f,f,f} | 0 | 0 | {f} | % | 0 | 100 |  |  | 2.5 | [11 empty] | {f} |  |  |  |  | >8
a202 | 38bc28d4-c13c-4a50-b514-2f75996dd08b | AO_SW_T_AMEV1 | 0-10V/4-20mA | X |  |  |  |  | X | X | 1.1.3; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Temperature (Hardware Connection) | {f,f,f,f} | 0 | 0 | {f} | °C | [0] | [50] |  |  | 0.5 | [11 empty] | {f} |  |  |  |  | >8
a203 | f2fb7788-7569-4c9e-bad7-9776d90ea72d | AO_SWC_T_AMEV1 | 0-10V/4-20mA | X |  |  |  |  | X | X | 1.1.3; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Temperature calculated (hardware connection) | {f,f,f,f} | 0 | 0 | {f} | °C | [0] | [50] |  |  | 0.5 | [11 empty] | {f} |  |  |  |  | >8
a204 | 602ac6eb-b36d-443f-891c-3337f04fc162 | AO_SW_F_AMEV1 | 0-10V/4-20mA | X |  |  |  |  | X | X | 1.1.3; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Volume flow | {f,f,f,f} | 0 | 0 | {f} | m³/h |  |  |  | specify | >0 | [11 empty] | {f}
a205 | 6dc8473a-8b77-44a4-b339-84b687ae6bb2 | AO_SW_PD_AMEV1 | 0-10V/4-20mA | X |  |  |  |  | X | X | 1.1.3; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Conveying head | {f,f,f,f} | 0 | 0 | {f} | m | [0] | [10] |  |  | 0.2 | [11 empty] | {f} |  |  |  |  | >8
a206 | 22995b24-b076-41f8-be55-17ede4d38b36 | AO_MWC_J_AMEV1 | 0-10V/4-20mA | X |  |  |  |  | X | X | 1.1.3; 3.1.1; 3.1.3 | [UAK] | [Description] | Power calculated Reading (energy feed-in) | {f,f,f,f} | 0 | 0 | {f} | % | 0 | 100 |  |  | 2.5 | [11 empty] | {f} |  |  |  |  | >8
a301 | fa350b5d-0aaa-4789-824c-86a0f145ce3c | AV_ST_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setting signal | {f,f,f,f} | 0 | 0 | {f} | % | 0 | 100 |  |  | 2.5 | [11 empty] | {f} |  |  |  |  | >8
a302 | a77a1e27-eba8-4e83-b913-a73745467cc8 | AV_RW_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Feedback value | {f,f,f,f} | 0 | 0 | {f} | % | 0 | 100 |  |  | 2.5 | [11 empty] | {f} |  |  |  |  | >8
[5 empty] | X |  |  |  | X | X
a303 | 5e0c8196-ffac-4211-9a85-7c796cd52da1 | AV_SW_T_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Temperature | {f,f,f,f} | 0 | 0 | [5 empty] | specify | >0 | 1 | 500 | specify | specify | 0.5 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a304 | a07256bd-b829-4aac-83be-0c0f069eed1b | AV_SW_TH_RU_S_AMEV1 | P<E |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Temperature heating Protection | {f,f,f,f} | 0 | 0 |  | °C | 5 | 15 |  | 6 | 0.1 | 1 | 500 | 5 | 15 | 0.5 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a305 | cd54f20f-b585-4aca-a7a9-03e98eaf4aed | AV_SW_TH_RU_E_AMEV1 | E<PK |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Temperature heating Economy (Lowering Mode) | {f,f,f,f} | 0 | 0 |  | K | [-10] | [-6] |  | [-8] | 0.1 | 1 | 500 | [-10] | [-6] | 0.1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a306 | 9333b7ce-66ff-40c0-811c-f8f956c1f2b9 | AV_SW_TH_RU_P_AMEV1 | PK<K |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Temperature heating Pre-Comfort (Absent) | {f,f,f,f} | 0 | 0 |  | K | [-6] | [-4] |  | [-4] | 0.1 | 1 | 500 | [-6] | [-4] | 0.1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a307 | 929e22e8-9367-4dba-87cd-f787f05426ad | AV_SW_TH_RU_K_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Temperature heating Comfort | {f,f,f,f} | 0 | 0 |  | K | [-4] | [0] |  | [-2] | 0.1 | 1 | 500 | [-4] | [0] | 0.1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a308 | ec9a4ea9-8bfe-48c6-8e5d-bc9cfe7116c1 | AV_SW_T_RU_B_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Temperature Basis | {f,f,f,f} | 0 | 0 |  | °C | [20] | [24] |  | [22] | 0.1 | 1 | 500 | [20] | [24] | 0.1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a309 | 8add1bac-b43d-4e41-8c02-c8432d10f033 | AV_SW_T_RU_V_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Temperature Adjustment | {f,f,f,f} | 0 | 0 |  | °C | [-3] | [3] |  | [0] | [12 empty] | {t} |  |  | 1 |  | >8 | AMEV1.1
a310 | 1c61a6fe-db6f-4657-bbdb-afeeb813a768 | AV_SW_TK_RU_K_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Temperature cooling Comfort | {f,f,f,f} | 0 | 0 |  | K | [2] | [4] |  | [+2] | 0.1 | 1 | 500 | [2] | [4] | 0.1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a311 | 0d44739c-5798-4e35-8819-2adfb9396a5e | AV_SW_TK_RU_P_AMEV1 | PK>K |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Temperature cooling Pre-Comfort | {f,f,f,f} | 0 | 0 |  | K | [4] | [6] |  | [+4] | 0.1 | 1 | 500 | [4] | [6] | 0.1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a312 | dd7b5a4f-1803-4aaa-93f7-4b3f8e31d1a5 | AV_SW_TK_RU_E_AMEV1 | E>PK |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Temperature cooling Economy | {f,f,f,f} | 0 | 0 |  | K | [6] | [10] |  | [+8] | 0.1 | 1 | 500 | [6] | [10] | 0.1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a313 | 004c44a7-6eec-471c-a17a-aac79d275fb5 | AV_SW_TK_RU_S_AMEV1 | P>E |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Temperature cooling Protection | {f,f,f,f} | 0 | 0 |  | °C |  |  |  | 40 | 0.1 | 1 | 500 | 40 | 42 | 0.5 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a314 | 6aea1451-12f9-4b84-bcaa-4fbb0f7f2c6e | AV_SW_T_RU_V_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Temperature Adjuster | {f,f,f,f} | 0 | 0 |  | K | [-3] | [3] |  | [0] | 0.5 | 1 | 500 | [-3] | [3] | 0.5 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a315 | a8e3bea2-da65-4939-ac73-f9fa37578602 | AV_SWC_TH_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Temperature heating Calculated | {f,f,f,f} | 0 | 0 | {f} | °C |  |  |  |  | 0.5 | [11 empty] | {f} |  |  | 1 |  | >8
a316 | 2ae99910-a66d-45f7-86a8-018596801445 | AV_SWC_TK_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Temperature cooling Calculated | {f,f,f,f} | 0 | 0 | {f} | °C |  |  |  |  | 0.5 | [11 empty] | {f} |  |  | 1 |  | >8
a317 | 4af8731c-8fd0-4d9d-b288-1700a5054516 | AV_SW_M_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Humidity | {f,f,f,f} | 0 | 0 |  | %rF |  |  |  | specify | 0.5 | 1 | 500 | specify | specify | 2 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a318 | c20790af-4a0f-4c99-afdd-4892877395ae | AV_SW_ME_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Humidity dehumidification | {f,f,f,f} | 0 | 0 |  | %rF |  |  |  | 65% | 0.5 | 1 | 500 | [60] | [70] | 2 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a319 | 89bb90cf-2e59-4d2d-aa5f-8d1f453094a9 | AV_SW_MB_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Humidity moistening | {f,f,f,f} | 0 | 0 |  | %rF |  |  |  | 30% | 0.5 | 1 | 500 | [25] | [35] | 2 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a320 | 91ecbf73-3f95-4456-aec3-9a79bafa14b9 | AV_SWC_X_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Humidity calculated | {f,f,f,f} | 0 | 0 | {f} | g/kg |  |  |  |  | 0.1 | [11 empty] | {f} |  |  | 1 |  | >8
a321 | 868cbb23-9ab8-4def-b3a8-cdb90c924079 | AV_SWC_XE_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Humidity dehumidification calculated | {f,f,f,f} | 0 | 0 | {f} | g/kg |  |  |  |  | 0.1 | [11 empty] | {f} |  |  | 1 |  | >8
a322 | a4df2f83-f6ea-4ca5-a3a2-e7eb0d3b2a9e | AV_SWC_XB_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Humidity moistening calculated | {f,f,f,f} | 0 | 0 | {f} | g/kg |  |  |  |  | 0.1 | [11 empty] | {f} |  |  | 1 |  | >8
a323 | 6a6ebd18-5a1b-4de1-abdc-386f8cd41449 | AV_SW_P_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Pressure | {f,f,f,f} | 0 | 0 | [6 empty] | specify | specify | 300 | specify | specify |  | not NULL | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a324 | 1232b805-69b4-4e01-b98a-d23a414281fb | AV_SW_P_L_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Pressure | {f,f,f,f} | 0 | 0 |  | Pa |  |  |  |  | [30] | 120 | 300 | [0] | [500] | [30] | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a325 | 45e86ba4-2889-4a4f-a107-6b2c8c65686b | AV_SW_P_H_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Pressure | {f,f,f,f} | 0 | 0 |  | bar |  |  |  |  | 0.1 | 30 | 300 | [1,5] | [5] | 0.1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a326 | 139663c0-7552-4238-9d7a-94d3ea8f9c28 | AV_SW_PD_L_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Pressure difference | {f,f,f,f} | 0 | 0 |  | Pa |  |  |  |  | [150/3] | 120 | 300 | [0/-40] | [500/40] | [150/3] | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a327 | e45c1a2e-d734-4b23-807a-e896c9cc2267 | AV_SW_PD_H_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Pressure difference | {f,f,f,f} | 0 | 0 |  | bar |  |  |  |  | 0.1 | 30 | 300 | [1,5] | [5] | 0.1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a328 | 793af15c-dddd-4c81-8394-4d2a1415956e | AV_SW_F_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Volume flow | {f,f,f,f} | 0 | 0 |  | m³/h |  |  |  | specify | >0 | 1 | 500 | specify | specify | [10] | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a329 | 3b7086b0-42ec-4606-a22b-6fdb3c130802 | AV_SW_QCD_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Air quality CO2 | {f,f,f,f} | 0 | 0 |  | ppm |  |  |  |  | [10] | 1 | 300 | [800] | [1200] | [10] | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a330 | 2c975540-bd4e-4e87-b944-3e693d0bccd1 | AV_SW_Q_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Air quality IAQ (indoor air quality) | {f,f,f,f} | 0 | 0 |  | % |  |  |  |  | [1] | 1 | 300 |  | [50] | [1] | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a331 | 5e67c035-148f-4d90-96ba-3cfe6ac0f19d | AV_SW_QVO_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Air quality VOC | {f,f,f,f} | 0 | 0 |  | % |  |  |  |  | [1] | 1 | 300 |  | [50] | [1] | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a332 | 9b95296c-90f7-430d-b726-0d1f5b52cc81 | AV_SW_25QPF_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Air quality Particulate Matter 2.5 | {f,f,f,f} | 0 | 0 |  | µg/m³ |  |  |  |  | [1] | 1 | 300 |  | [25] | [1] | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a333 | 6574e262-8e08-4770-80a6-2fdba2fc5164 | AV_SW_10QPF_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Air quality Particulate Matter 10 | {f,f,f,f} | 0 | 0 |  | µg/m³ |  |  |  |  | [1] | 1 | 300 |  | [50] | [1] | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a334 | ef0e547c-75f2-49e7-8708-2e819ed0f1bb | AV_ST_E_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Lighting | {f,f,f,f} | 0 | 0 |  | % |  |  |  |  | [2,5] | [11 empty] | {t} |  |  | 1 |  | >8
a335 | 29a66529-29f2-4be7-9206-c7298598b394 | AV_ST_ER_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Lighting Reduced | {f,f,f,f} | 0 | 0 |  | % |  |  |  |  | [2,5] | [11 empty] | {t} |  |  | 1 |  | >8
a336 | 4df92393-fbf8-43aa-bcb0-ddd262ec2725 | AV_SW_E_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Illuminance | {f,f,f,f} | 0 | 0 |  | lux |  |  |  |  | [25] | 1 | 300 | [100] | [600] | [10] | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a337 | f40af017-2287-4357-a384-cb9fbc446589 | AV_SW_ER_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Illuminance Reduced | {f,f,f,f} | 0 | 0 |  | lux |  |  |  |  | [25] | [11 empty] | {t} |  |  | 1 |  | >8
a338 | 1e727c70-3064-44de-b73d-dbf3c06ea6b8 | AV_SW_POS_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Position | {f,f,f,f} | 0 | 0 |  | % |  |  |  |  | [2,5] | [11 empty] | {t} |  |  | 1 |  | >8
a339 | 02564efb-00ce-4ec3-b4ae-ae99d8227ced | AV_SW_WIN_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setpoint Angle | {f,f,f,f} | 0 | 0 |  | ° |  |  |  |  | [5] | [11 empty] | {t} |  |  | 1 |  | >8
a340 | 65dbd921-1604-4eba-b6e1-237904a3a5f7 | AV_ST_POS_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setting Signal Position | {f,f,f,f} | 0 | 0 |  | % |  |  |  |  | [2,5] | [11 empty] | {t} |  |  | 1 |  | >8
a341 | 59183b39-faf2-469e-a532-02ff3f635ff6 | AV_ST_WIN_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Setting Signal Angle | {f,f,f,f} | 0 | 0 |  | ° |  |  |  |  | [5] | [11 empty] | {t} |  |  | 1 |  | >8
a342 | 37977761-1d25-45e8-bb09-44f83db4c80a | AV_MW_T_AMEV1 | communicative |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Temperature Reading | {f,f,f,f} | 0 | 0 | {f} | °C |  |  |  | 0 | 0.5 | 60 | 300 | [5] | [40] | 0.5 | {t,t} | {t,t,t} | Alarm | * | * | *** | {f} |  |  |  |  | >8
a343 | 454cac39-0911-4a47-9298-352c8a72cb41 | AV_MW_T_AU_AMEV1 | communicative, outdoor |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Temperature Reading | {f,f,f,f} | 0 | 0 | {f} | °C |  |  |  | 0 | 0.2 | [11 empty] | {f} |  |  |  |  | >8
a344 | eafc4935-10ac-422f-8252-b9045ed3bd6e | AV_MWC_TD_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Temperature difference Reading calculated | {f,f,f,f} | 0 | 0 | {f} | K |  |  |  | 0 | [0,2] | [11 empty] | {f} |  |  |  |  | >8
a345 | bb187aab-9b02-4c62-a7c2-3b7880e174ff | AV_MW_M_AU_AMEV1 | communicative, outdoor |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Relative humidity Reading | {f,f,f,f} | 0 | 0 | {f} | %r.F. |  |  |  | 0 | 3 | [11 empty] | {f} |  |  |  |  | >8
a346 | 0e6b1f8a-fa03-48f2-9452-3b471aca1997 | AV_MW_F_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Volume flow Reading | {f,f,f,f} | 0 | 0 | {f} | m³/h |  |  |  | 0 | [25] | [11 empty] | {f} |  |  |  |  | >8
a347 | e70cb5db-3f4f-4f91-b3f0-0301e876a36b | AV_MW_DMZ_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Volume Flow Steam Reading | {f,f,f,f} | 0 | 0 | {f} | [to/h]* |  |  |  | 0 | [1] | [11 empty] | {f} |  |  |  |  | >8
a348 | 8ea8ea92-3202-406e-82f5-3fe49af2e05d | AV_ZW_F_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Quantity Reading | {f,f,f,f} | 0 | 0 | {f} | m³ |  |  |  | 0 | [1] | [11 empty] | {f} |  |  |  |  | >8
a349 | 2fbefa74-9ddb-4aaa-9778-f2cf59477eec | AV_MWC_GTZ_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Degree Day Number Reading calculated | {f,f,f,f} | 0 | 0 | {f} | Kd |  |  |  | 0 | 0.1 | [11 empty] | {f} |  |  |  |  | >8
a350 | f1ec52c1-c161-476c-88e2-33e6d84d3baa | AV_MWC_WG_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Efficiency (COP) Reading calculated | {f,f,f,f} | 0 | 0 | {f} |  |  |  |  | 0 | 0.1 | [5 empty] | {f,f} | {f,t,f} |  |  |  |  | {f} |  |  |  |  | >8
a351 | efa41d69-1f94-47f4-aa91-d7fc27d66e99 | AV_MWC_RWZ_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Return heat coefficient Reading calculated | {f,f,f,f} | 0 | 0 | {f} |  |  |  |  | 0 | [2,5] | 900 | 300 | [73] |  | 1 | {t,f} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a352 | 7ea94aff-14df-47ce-b111-aa2df1cef9ac | AV_MW_WIG_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Wind speed Reading | {f,f,f,f} | 0 | 0 | {f} | m/s |  |  |  | 0 | [2,5] | [11 empty] | {f} |  |  |  |  | >8
a353 | 7e5f7adf-6742-4309-b63b-d739abfeef69 | AV_MWC_WIG_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Wind speed Reading Calculated | {f,f,f,f} | 0 | 0 | {f} | m/s |  |  |  | 0 | [2,5] | [11 empty] | {f} |  |  |  |  | >8 | AMEV1.1
a354 | 51d19626-6a73-480d-a79c-9598a3337b93 | AV_MW_WIR_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Wind direction/Position of Sun | {f,f,f,f} | 0 | 0 | {f} | ° |  |  |  | 0 | [5] | [11 empty] | {f} |  |  |  |  | >8
a355 | cde95bc7-817f-4a8a-a62b-f8d431d47af8 | AV_MWC_WIR_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Wind direction Reading calculated | {f,f,f,f} | 0 | 0 | {f} | ° | 0 | 360 |  | 0 | [5] | [11 empty] | {f} |  |  |  |  | >8 | AMEV1.1
[5 empty] | X |  |  |  | X | X
a356 | f26f9f12-0f15-4480-9cea-60d64938b96f | AV_MW_E_RU_AMEV1 | communicative, room |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Illuminance Reading | {f,f,f,f} | 0 | 0 | {f} | lx |  |  |  | 0 | 50 | [11 empty] | {f} |  |  |  |  | >8
a357 | d0a64df9-ce90-4221-8262-464aa81f7dde | AV_MW_E_AU_AMEV1 | communicative, outdoor |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Illuminance Reading | {f,f,f,f} | 0 | 0 | {f} | klx |  |  |  | 0 | [5] | [11 empty] | {f} |  |  |  |  | >8
a358 | e863528b-f406-4304-b75c-74943af8e925 | AV_MW_R_AU_AMEV1 | communicative, outdoor |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Global radiation Reading | {f,f,f,f} | 0 | 0 | {f} | W/m² |  |  |  | 0 | [5] | [11 empty] | {f} |  |  |  |  | >8
a359 | 1a061bfb-2284-45a1-8e20-c3c63b8e88a0 | AV_MW_ALxN_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Voltage Reading | {f,f,f,f} | 0 | 0 | {f} | V |  |  |  | 0 | 5 | 5 | 300 | [207] | [253] | 1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 0 |  | >8
a360 | beabcea7-b85e-4d95-8bca-296011e0baeb | AV_MW_C_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Current Reading | {f,f,f,f} | 0 | 0 | {f} | A |  |  |  | 0 | [] | [60] | 300 | 0 | [] | [] | {f,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 0 |  | >8
a361 | 715dd801-b490-4ebf-b63f-96cc5079318a | AV_MW_S_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Frequency Reading | {f,f,f,f} | 0 | 0 | {f} | Hz |  |  |  | 0 | 0.1 | 5 | 300 | [47,5] | [52,5] | 0.1 | {t,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 0 |  | >8
a362 | 4b4683ec-ae63-4cf5-acc9-0f96fdf87a51 | AV_MW_J_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Active power Reading | {f,f,f,f} | 0 | 0 | {f} | [kW]* |  |  |  | 0 | [] | [60] | 300 | 0 | [] | [] | {f,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 0 |  | >8
a363 | 30ae53c1-68d3-4c83-a640-ef0832210737 | AV_MW_COS_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Power factor Reading | {f,f,f,f} | 0 | 0 | {f} |  |  |  |  | 0 | 0.05 | [60] | 300 | [0,8] | [1] | 0.1 | {t,f} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 0 |  | >8
a364 | c8a41c6b-8c08-4127-80f5-70df11367e39 | AV_MW_POS_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Position Reading | {f,f,f,f} | 0 | 0 | {f} | % |  |  |  | 0 | [2,5] | [11 empty] | {f} |  |  |  |  | >8
a365 | a0e46371-7f8f-4a23-8ab7-88f602602ccc | AV_MW_WIN_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Angle Reading | {f,f,f,f} | 0 | 0 | {f} | ° |  |  |  | 0 | [5] | [11 empty] | {f} |  |  |  |  | >8
a366 | 6460d920-6032-4a7e-ba79-41c23695176e | AV_MWC_POS_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Position Reading calculated | {f,f,f,f} | 0 | 0 | {f} | % |  |  |  | 0 | [2,5] | [11 empty] | {f} |  |  |  |  | >8
a367 | 47943f97-31c0-4645-84da-68795893a8b2 | AV_MWC_WIN_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Angle Reading calculated | {f,f,f,f} | 0 | 0 | {f} | ° |  |  |  | 0 | [5] | [11 empty] | {f} |  |  |  |  | >8
a368 | 132383a3-20b1-484a-a6ce-866088c69ed6 | AV_ZAF_LAM_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Cabin load Reading | {f,f,f,f} | 0 | 0 | {f} | kg | 0 | [630] |  | 0 | 75 | 1 | 800 | 0 | [630] | 1 | {f,t} | {t,t,t} | Event | * | * |  | {t} |  |  | 1 |  | >8
a369 | dfb6d6c5-4572-4374-b137-6160157e97dd | AV_ZAF_S_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Cabin speed Reading | {f,f,f,f} | 0 | 0 | {f} | m/s | 0 | [20] |  | 0 | [0,5] | [11 empty] | {f} |  |  |  |  | >8
a370 | 2ca4fefe-d5ff-4b11-910b-c241d643a32d | AV_ZAF_ABW_AMEV1 |  |  | X | X |  |  | X | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Deviation of stopping accuracy Reading | {f,f,f,f} | 0 | 0 | {f} | mm | [-150] | [150] |  | 0 | 1 | 1 | 300 | -10 | 10 | 1 | {f,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a371 | fcc58365-338e-4d0b-a570-81d3c03ef487 | AV_PAR_F_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Volume flow Parameter | {f,f,f,f} | 0 | 0 | {f} | m³/h | 0 |  |  | [VVR min] | [5] | [11 empty] | {f} |  |  |  |  | >8
a372 | 7b4e7de2-30d3-42bd-804c-80da2ee5bd95 | AV_PAR_K_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Time Parameter | {f,f,f,f} | 0 | 0 | {f} | s | 0 |  |  |  | 1 | [11 empty] | {f} |  |  |  |  | >8
a373 | 37237666-54c9-4278-ad23-3518324f6224 | AV_PAR_NL_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Delay time Parameter | {f,f,f,f} | 0 | 0 | {f} | s |  |  |  | specify | 1 | [11 empty] | {f} |  |  |  |  | >8
a374 | 8413e24b-e7a1-48e4-ad05-cc2518c4aa9d | AV_PAR_OHZ_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Hold-open time Parameter | {f,f,f,f} | 0 | 0 | {f} | s |  |  |  | specify | 1 | [11 empty] | {f} |  |  |  |  | >8
[5 empty] | X |  |  |  | X | X
a375 | 7179fff3-3551-4c25-9dac-7d8edd67ba0e | AV_ZW_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Count | {f,f,f,f} | 0 | 0 | {f} |  |  |  |  | 0 | [1] | [11 empty] | {f} |  |  |  |  | >8
a376 | 4d2ec8e3-f5ab-47f3-aafd-993674663080 | AV_ZW_H_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Counting value Consumption (or Feed-in/Production) | {f,f,f,f} | 0 | 0 | {f} | [kWh]* |  |  |  | 0 | [1] | [5 empty] | {f,f} | {f,t,t} | Alarm | * | * | *** | {t} |  |  | 0 |  | >8
a377 | 3ec64193-c816-4868-a631-5b055ae266da | AV_ZW_HVR_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Reactive work Count | {f,f,f,f} | 0 | 0 | {f} | [kvarh]* |  |  |  | 0 | [1] | [5 empty] | {f,f} | {f,t,t} | Alarm | * | * | *** | {t} |  |  | 0 |  | >8
a378 | 1b33c9ff-7db7-4f70-8180-b2eca61993a4 | AV_ZW_DMZ_AMEV1 |  |  | X |  |  |  | X | X | 1.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Counting value Consumption (or Feed-in/Production) | {f,f,f,f} | 0 | 0 | {f} | [to]* |  |  |  | 0 | [1] | [5 empty] | {f,f} | {f,t,t} | Alarm | * | * | *** | {t} |  |  | 0 |  | >8
a379 | 28c57476-d9cf-4886-8dab-1b783ff9357e | AV_MWC_ZFA_AMEV1 |  |  | X |  |  | X | X | X | 1.2.1; 2.2.3; 3.1.1; 3.1.3 | [UAK] | [Description] | Counter trips / openings | {f,f,f,f} | 0 | 0 | {f} |  | 0 |  |  | 0 | [1] |  | 400 |  | [] | 1 | {f,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a380 | 34396254-f208-438c-99bd-7c96ba15e91b | AV_SN_AMEV1 |  |  | X | X |  |  |  | X | 1.2.1; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Serial number | {f,f,f,f} | 0 | 0 | {f} |  |  |  |  | current SN | 1 | 0 | 420 | current SN | current SN |  | {f,f} | {f,t,t} | Alarm | * | * | *** | {t} |  |  | 0 |  | >8
a381 | 133198ef-0c03-46d1-a6b7-5b309547ffc8 | AV_MWC_BZ_AMEV1 |  |  | X |  | X |  | X | X | 1.2.1;2.2.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Hours | {f,f,f,f} | 0 | 0 | {f} | h | 0 |  |  | 0 | 1 | 1 | 400 | 0 | [8760] | 1 | {f,t} | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
|  | * B (Builder/Operator), P (Planning), X (Executing Company) | [9 empty] | Default value (parameterization) and test value | [6 empty] | [] => Default value (suggestion) | [13 empty] | * Can be used for testing in the 1:1 test
[12 empty] | Test value (internally generated value) | [6 empty] | * Units for meters should be uniform within the project | [13 empty] | *** Implementation in accordance with Chapter 4.4

## 8.3 BI
ObjSort + LfdNr | UUID | Objekt-Template- Kennung | Kommentar | GA-FL Einträge (1.1.2) | GA-FL Einträge (2.2.1) | GA-FL Einträge (3.1.1) | GA-FL Einträge (3.1.3) | GA-FL Einträge (Abschnitte/Spalten) | Object_Name | Description | Verwendung | Status_Flags | Event_State | Reliability | Out_Of_Service | Polarity | Inactive_Text | Active_Text | Change_Of_State_Count | Elapsed_Active_Time | Time_Delay | Notification_Class | Alarm_Value | Event_Enable | Notify_Type | Event_Time_Stamps | Event_Message_Texts | Event_Message_Texts_Config | Event_Detection_Enable | Event_Algorithm_Inhibit | Event_Algorithm_Inhibit_Ref | Time_Delay_Normal | Reliability_Evaluation_Inhibit | Letztmalige Änderung in Version
|  | PropSort | [6 empty] | a11 | a12 | [5 empty] | b12 | b13 | b14 |  |  | c43 | c11 | c16 | c12 | c13 |  |  | c14 | c15 | c41 | c42 | c44
|  | Conformance Code | [6 empty] | R | W |  | R | R | W1 | W | W | R | R | R0 | R0 | W | W | W | W | W | R | R | W | W | RA | RA | W | RX¦O
|  | Grundlegende Vorgabe * | [6 empty] | B * | B | [5 empty] | B | B | B |  |  | P | B | B | B | B |  |  | B | B | P | P | P
|  | Detailierte Festlegung * | [6 empty] | P * | P | [5 empty] | P | P | P |  |  | P | P | P | P | P |  |  | P | P | P | P | P
|  | Umsetzung * | [6 empty] | U * | U |  | U | U | U | U | U | U | U | U | U | U | U | U | U | U |  |  | U | U | U | U | U | U
|  | Vorgabewert (Parametrierung) | [6 empty] | ja | ja |  | nein | nein | nein | nein | ja | ja | ja | nein | nein | ja | ja | ja | ja | ja | nein | nein | ja | ja | nein | nein | ja | nein
Gefahr-/Störmeldungen
a401 | 65775987-1703-4600-967f-9774532bd519 | BI_GM_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Gefahrmeldung | {f,f,f,f} | 0 | 0 | {f} | reverse | Normal | Gefahr | >0* |  |  | 100/150 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | AMEV1.1
a402 | dfe6dd1b-03fb-4be0-b601-c36a561c8d55 | BI_GM_BSK_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Gefahrmeldung | {f,f,f,f} | 0 | 0 | {f} | reverse | Normal | Gefallen | >0* |  |  | 150 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | AMEV1.1
a403 | 9b6bc027-a1ed-4955-a4c7-d337d15a96cc | BI_SM_NOT_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Störmeldung | {f,f,f,f} | 0 | 0 | {f} | reverse | Normal | Not-Aus | >0* |  |  | 150 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a404 | 6a098119-80fc-44d5-81b0-c81b495be61c | BI_AM_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Alarmmeldung | {f,f,f,f} | 0 | 0 | {f} | reverse | Normal | Alarm | >0* |  |  | 200 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a405 | d32549bc-fc04-4530-a6e3-e6cc4d642e1d | BI_AM_ZOF_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Alarmmeldung | {f,f,f,f} | 0 | 0 | {f} | reverse | Zu | Auf | >0* |  | 1 | 200 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a406 | 0ab22326-35ea-484b-8b0a-498157fd15a2 | BI_SM_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Störmeldung | {f,f,f,f} | 0 | 0 | {f} | reverse | Normal | Störung | >0* |  |  | 300 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a407 | 52c405c3-23c9-4164-84bb-314b16c248f9 | BI_SM_NAF_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Störmeldung | {f,f,f,f} | 0 | 0 | {f} | reverse | Normal | Ausgefallen | >0* |  |  | 300 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a408 | 0ece8034-19b2-4b7b-9a21-e51c10331481 | BI_SM_LU_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Störmeldung | {f,f,f,f} | 0 | 0 | {f} | reverse | Normal | Ausgelöst | >0* |  |  | 300 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a409 | d6974ba7-5149-445d-aa93-4330b8d89d84 | BI_SM_SYS_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Störmeldung | {f,f,f,f} | 0 | 0 | {f} | reverse | Normal | Störung | >0* |  |  | 600 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a410 | 7a953dbd-b193-4490-b488-897463c8db03 | BI_SM_LU_IH_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Störmeldung | {f,f,f,f} | 0 | 0 | {f} | normal | Lufströmung | Keine Luftströmung | >0* | >0* | [60] | 200 | active | {t,t,t} | Alarm | * | * | *** | {t} | [*] | [*] | 1
a411 | 4a09abd1-0b60-4f4c-825f-d78e0309748b | BI_ANO_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Abnomal Meldung | {f,f,f,f} | 0 | 0 | {f} | normal | Normal | Anormal | >0* |  | [60] | 350 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a412 | 42c32275-414f-4a68-94ef-e75c25875b39 | BI_SAB_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Sabotagealarm | {f,f,f,f} | 0 | 0 | {f} | reverse | Normal | Sabotage | >0* |  |  | 150 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a458 | 5a2ce3d0-de11-419e-97e4-6e70c756108b | BI_GM_P_AMEV1.1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Gefahrmeldung Personen | {f,f,f,f} | 0 | 0 | {f} | reverse | Normal | Gefahr | >0* |  |  | 100 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | AMEV1.1
a459 | 3e72c567-be79-4bae-b60b-58a2e15089aa | BI_GM_L_AMEV1.1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Gefahrmeldung Liegenschaft | {f,f,f,f} | 0 | 0 | {f} | reverse | Normal | Gefahr | >0* |  |  | 150 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | AMEV1.1
Betriebsmeldungen
a413 | 34b26c5f-56fa-4256-b5aa-173b9c8978d7 | BI_BB_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Betriebsbereit | {f,f,f,f} | 0 | 0 | {f} | reverse | Bereit | Nicht Bereit |  | >0* |  | 300 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a414 | c6995422-eac8-45df-b3fb-afbac00c6853 | BI_BM_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Betriebsmeldung | {f,f,f,f} | 0 | 0 | {f} | normal | Aus | Ein |  | >0* | [8 empty] | {f}
a415 | ef45dc69-79ed-40d6-9833-2e93f671c10e | BI_BM_AS_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Betriebsmeldung Stufe "x" | {f,f,f,f} | 0 | 0 | {f} | normal | --- | Stufe "x" |  | >0* | [8 empty] | {f}
a416 | fdf9079c-a27f-47ee-aa67-0647efdf41cf | BI_BM_AFR_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Betriebsmeldung | {f,f,f,f} | 0 | 0 | {f} |  | Aus | Freigabe |  | >0* | [8 empty] | {f}
a417 | 73feda32-622c-4e71-ad43-54b7c557c90b | BI_BM_AF_AMEV1.1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Betriebsmeldung Angefordert | {f,f,f,f} | 0 | 0 | {f} | normal | Aus | Angefordert |  | >0* | [8 empty] | {f} |  |  |  |  | AMEV1.1
a418
a419 | 835f3b2c-90d1-4d5d-b272-568ab1bedca9 | BI_BM_GOL_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Betriebsmeldung | {f,f,f,f} | 0 | 0 | {f} |  | Gas | Öl |  | >0* | [8 empty] | {f}
a420 | d2f6a37a-183f-417e-bac3-d61ebcd71634 | BI_BM_HKL_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Betriebsmeldung | {f,f,f,f} | 0 | 0 | {f} |  | Heizen | Kühlen |  | >0* | [8 empty] | {f}
a421 | 156709d2-acea-426d-8857-a098e0797df1 | BI_BM_LFN_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Betriebsmeldung | {f,f,f,f} | 0 | 0 | {f} |  | Lokal | Fern |  | >0* | [8 empty] | {f}
a422 | 35d06169-858b-452a-bfd5-b19e3a9d33d1 | BI_BM_LRE_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Betriebsmeldung | {f,f,f,f} | 0 | 0 | {f} |  | Links | Rechts |  | >0* | [8 empty] | {f}
a423 | 9b46266a-f9d5-42e3-a0a0-8f6672132276 | BI_BM_NAN_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Betriebsmeldung | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Anormal |  | >0* | [8 empty] | {f}
a424 | 134c04c7-d86a-4f82-9e99-24d793b739c2 | BI_BM_NU_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Betriebsmeldung | {f,f,f,f} | 0 | 0 | {f} |  | Netz A | Netz B |  | >0* | [8 empty] | {f}
a425
a426 | b258cd2f-5b9f-429b-87cd-b144a6224d38 | BI_BM_NLA_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Betriebsmeldung | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Ausgelastet |  | >0* | [8 empty] | {f}
a427 | 3c7fb6c1-f54a-44c8-a3c5-9f2ebb4e5fff | BI_BM_NOT_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Betriebsmeldung | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Notbetrieb |  | >0* | [8 empty] | {f}
a428 | f1f1d8cc-ed03-4330-92bc-ecf1e87362f1 | BI_BM_NRZ_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Betriebsmeldung | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Reduziert |  | >0* | [8 empty] | {f}
a429 | 9da3efd2-ae36-4e55-99f0-17503ade45d8 | BI_BM_NSP_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Betriebsmeldung | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Gesperrt |  | >0* | [8 empty] | {f}
a430 | f30af656-7cb4-4520-89ac-de6b3c144ce5 | BI_BM_NTG_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Betriebsmeldung | {f,f,f,f} | 0 | 0 | {f} |  | Absenkbetrieb | Komfort |  | >0* | [8 empty] | {f}
a431 | c40cf18b-2fce-4277-8495-4613b6a75524 | BI_BM_PA_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Betriebsmeldung | {f,f,f,f} | 0 | 0 | {f} |  | --- | Auf |  | >0* | [8 empty] | {f}
a432 | 5f7b30dd-3c92-43f2-8e3d-eaabc11a1cc4 | BI_BM_PAK_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Betriebsmeldung | {f,f,f,f} | 0 | 0 | {f} |  | Passiv | Aktiv |  | >0* | [8 empty] | {f}
a433 | 976eb7de-b646-4811-9c8a-e655988cce26 | BI_BM_PZ_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Betriebsmeldung | {f,f,f,f} | 0 | 0 | {f} |  | --- | Zu |  | >0* | [8 empty] | {f}
a434 | ce00fdac-1947-4906-8d9a-8577a0dd3827 | BI_BM_SEP_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Betriebsmeldung | {f,f,f,f} | 0 | 0 | {f} |  | Startposition | Endposition |  | >0* | [8 empty] | {f}
a435 | 267ef0fe-2efb-4578-8523-9fff993b257b | BI_BM_VHO_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Betriebsmeldung | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Hoch |  | >0* | [8 empty] | {f}
a436 | 12783c14-be54-4f1d-b883-1abfeee9f37d | BI_BM_VTI_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Betriebsmeldung | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Tief |  | >0* | [8 empty] | {f}
a437 | dbb832e7-50f8-4f58-a1dd-58561b1060c6 | BI_BM_VZH_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Betriebsmeldung | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Zu Hoch |  | >0* | [8 empty] | {f}
a438 | 39d1a987-6e50-4ba4-845f-145651b37579 | BI_BM_VZT_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Betriebsmeldung | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Zu Tief |  | >0* | [8 empty] | {f}
a439 | 903c18a6-631f-41a0-96f1-db766d9d4c70 | BI_BM_WSO_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Betriebsmeldung | {f,f,f,f} | 0 | 0 | {f} |  | Winter | Sommer |  | >0* | [8 empty] | {f}
a440 | 4850c7d3-569f-4c9b-84c4-45d80db90147 | BI_BM_ZOF_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Betriebsmeldung | {f,f,f,f} | 0 | 0 | {f} |  | Zu | Auf |  | >0* | [8 empty] | {f}
a441
Rückmeldungen
a442 | c8bb6588-f7e3-4d4b-946e-5cf5e777a236 | BI_RM_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Rückmeldung | {f,f,f,f} | 0 | 0 | {f} | normal | Zu | Auf |  | >0* | [8 empty] | {f}
a443 | 9be71529-9e12-4477-bbad-74108f2f72bc | BI_RM_A_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Rückmeldung Auf | {f,f,f,f} | 0 | 0 | {f} | normal | Passiv | Auf |  | >0* | [8 empty] | {f}
a444 | 9af4e857-8a13-4a59-8884-77885254dca2 | BI_RM_Z_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Rückmeldung Zu | {f,f,f,f} | 0 | 0 | {f} | normal | Passiv | Zu |  | >0* | [8 empty] | {f}
a445 | 33fbb59d-0a40-4731-925a-b9672648200e | BI_RM_E_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Rückmeldung Ein | {f,f,f,f} | 0 | 0 | {f} | normal | Passiv | Ein |  | >0* | [8 empty] | {f}
a446 | e392203e-5fe1-4715-9e54-631941bb4a02 | BI_RM_S_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Rückmeldung Aus | {f,f,f,f} | 0 | 0 | {f} | normal | Passiv | Aus |  | >0* | [8 empty] | {f}
a447 | b084463a-fe50-481b-90b4-bce1d2628a07 | BI_RM_AK_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Rückmeldung | {f,f,f,f} | 0 | 0 | {f} | normal | Aus | Ein |  | >0* | [8 empty] | {f}
a448 | b28faa46-7717-4e7b-93a8-c982604bd99e | BI_RM_NJ_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Rückmeldung | {f,f,f,f} | 0 | 0 | {f} | normal | Nein | Ja |  | >0* | [8 empty] | {f}
a449 | 8707a872-a167-4363-ba85-0d75b0815f3e | BI_RM_IO_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Rückmeldung in Ordnung | {f,f,f,f} | 0 | 0 | {f} | normal | In Ordnung | Abweichung |  | >0* | [8 empty] | {f}
a450 | 40a81211-2cfa-4c3c-9775-a80f4e9dca47 | BI_PAE_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Rückmeldung Präsenz | {f,f,f,f} | 0 | 0 | {f} | normal | Nicht Präsenz | Präsenz |  | >0* | [8 empty] | {f}
a451 | dd2680c0-1ccc-4ac9-a10a-4efe86c76043 | BI_ENT_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Entriegelung | {f,f,f,f} | 0 | 0 | {f} | normal | Inaktiv | Aktiv |  | >0* | 0 | 500 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a452 | c66d9b08-d2fb-4543-8491-acf5474c2967 | BI_VRR_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Verrriegelung | {f,f,f,f} | 0 | 0 | {f} | normal | Inaktiv | Aktiv |  | >0* | 0 | 600 | active | {t,t,t} | Event | * | * | *** | {t} |  |  | 1
Wartungs-/Handmeldungen
a453 | f4894ea4-2d89-4aa0-9195-6e04dd467467 | BI_WM_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Wartungsmeldung | {f,f,f,f} | 0 | 0 | {f} | normal | Normal | Wartung | >0* |  |  | 400 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a454 | 0d36d9ae-4e64-4c79-8e15-7f6361146ddb | BI_WM_FI_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Wartungsmeldung Filter | {f,f,f,f} | 0 | 0 | {f} | normal | Normal | Aktiv | >0* |  |  | 425 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a455 | 2af0c66a-b562-42f7-93b6-1e3954231498 | BI_WM_REP_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Reparaturschalter | {f,f,f,f} | 0 | 0 | {f} | normal | Inaktiv | Aktiv | >0* |  |  | 400 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a456 | 102d3257-a732-4a3e-99e0-7d8988cdc658 | BI_RVM_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Revisionsmeldung | {f,f,f,f} | 0 | 0 | {f} | normal | Inaktiv | Revision | >0* |  |  | 450 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a457 | d608082b-79b9-4098-b1a2-db2738a012d1 | BI_HD_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Handmeldung | {f,f,f,f} | 0 | 0 | {f} | normal | Auto | Hand | >0* |  |  | 500 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
|  | * B (Bauherr/Betreiber), P (GA-Planung), U (Ausführendes Unternehmen) | [6 empty] | Vorgabewert (Parametrierung) und Prüfwert | [9 empty] | * Kann zur Prüfung beim 1:1 Test benutzt werden | [8 empty] | *** gemäß Kapitel 4.4 einrichten
[9 empty] | Prüfwert (systemintern erzeugter Wert) | [15 empty] | [*] Alarmierung bei abgeschalteter Anlage unterdrücken
ENGLISH VERSION (Draft)
ObjSort + No. | UUID | Object Template Identifier | Comment | BACS FL entries (1.1.2) | BACS FL entries (2.2.1) | BACS FL entries (3.1.1) | BACS FL entries (3.1.3) | BACS FL entries (sections/columns) | Object_Name | Description | Application | Status_Flags | Event_State | Reliability | Out_Of_Service | Polarity | Inactive_Text | Active_Text | Change_Of_State_Count | Elapsed_Active_Time | Time_Delay | Notification_Class | Alarm_Value | Event_Enable | Notify_Type | Event_Time_Stamps | Event_Message_Texts | Event_Message_Texts_Config | Event_Detection_Enable | Event_Algorithm_Inhibit | Event_Algorithm_Inhibit_Ref | Time_Delay_Normal | Reliability_Evaluation_Inhibit | Last change in version
|  | PropSort | [6 empty] | a11 | a12 | [5 empty] | b12 | b13 | b14 |  |  | c43 | c11 | c16 | c12 | c13 |  |  | c14 | c15 | c41 | c42 | c44
|  | Conformance Code | [6 empty] | R | W |  | R | R | W1 | W | W | R | R | R0 | R0 | W | W | W | W | W | R | R | W | W | RA | RA | W | RX¦O
|  | Basic spezification * | [6 empty] | B * | B | [5 empty] | B | B | B |  |  | P | B | B | B | B |  |  | B | B | P | P | P
|  | Detailed definition * | [6 empty] | P * | P | [5 empty] | P | P | P |  |  | P | P | P | P | P |  |  | P | P | P | P | P
|  | Implementation * | [6 empty] | X * | X |  | X | X | X | X | X | X | X | X | X | X | X | X | X | X |  |  | X | X | X | X | X | X
|  | Default value (parameterization) | [6 empty] | yes | yes |  | no | no | no | no | yes | yes | yes | no | no | yes | yes | yes | yes | yes | no | no | yes | yes | no | no | yes | no
Hazard/fault messages
a401 | 65775987-1703-4600-967f-9774532bd519 | BI_GM_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Hazard Alarm | {f,f,f,f} | 0 | 0 | {f} | reverse | Normal | Danger | >0* |  |  | 100/150 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | AMEV1.1
a402 | dfe6dd1b-03fb-4be0-b601-c36a561c8d55 | BI_GM_BSK_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Hazard Alarm | {f,f,f,f} | 0 | 0 | {f} | reverse | Normal | Fallen | >0* |  |  | 150 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | AMEV1.1
a403 | 9b6bc027-a1ed-4955-a4c7-d337d15a96cc | BI_SM_NOT_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Fault message | {f,f,f,f} | 0 | 0 | {f} | reverse | Normal | Emergency Stop | >0* |  |  | 150 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a404 | 6a098119-80fc-44d5-81b0-c81b495be61c | BI_AM_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Alarm message | {f,f,f,f} | 0 | 0 | {f} | reverse | Normal | Alarm | >0* |  |  | 200 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a405 | d32549bc-fc04-4530-a6e3-e6cc4d642e1d | BI_AM_ZOF_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Alarm message | {f,f,f,f} | 0 | 0 | {f} | reverse | Closed | Open | >0* |  | 1 | 200 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a406 | 0ab22326-35ea-484b-8b0a-498157fd15a2 | BI_SM_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Fault message | {f,f,f,f} | 0 | 0 | {f} | reverse | Normal | Fault | >0* |  |  | 300 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a407 | 52c405c3-23c9-4164-84bb-314b16c248f9 | BI_SM_NAF_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Fault message | {f,f,f,f} | 0 | 0 | {f} | reverse | Normal | Out | >0* |  |  | 300 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a408 | 0ece8034-19b2-4b7b-9a21-e51c10331481 | BI_SM_LU_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Fault message | {f,f,f,f} | 0 | 0 | {f} | reverse | Normal | Triggered | >0* |  |  | 300 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a409 | d6974ba7-5149-445d-aa93-4330b8d89d84 | BI_SM_SYS_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Fault message | {f,f,f,f} | 0 | 0 | {f} | reverse | Normal | Fault | >0* |  |  | 600 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a410 | 7a953dbd-b193-4490-b488-897463c8db03 | BI_SM_LU_IH_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Fault message | {f,f,f,f} | 0 | 0 | {f} | normal | Air flow | No Air flow | >0* | >0* | [60] | 200 | active | {t,t,t} | Alarm | * | * | *** | {t} | [*] | [*] | 1
a411 | 4a09abd1-0b60-4f4c-825f-d78e0309748b | BI_ANO_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Abnomal message | {f,f,f,f} | 0 | 0 | {f} | normal | Normal | Abnormal | >0* |  | [60] | 350 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a412 | 42c32275-414f-4a68-94ef-e75c25875b39 | BI_SAB_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Tamper alarm | {f,f,f,f} | 0 | 0 | {f} | reverse | Normal | Tamper | >0* |  |  | 150 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a458 | 5a2ce3d0-de11-419e-97e4-6e70c756108b | BI_GM_P_AMEV1.1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Danger People | {f,f,f,f} | 0 | 0 | {f} | reverse | Normal | Danger | >0* |  |  | 100 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | AMEV1.1
a459 | 3e72c567-be79-4bae-b60b-58a2e15089aa | BI_GM_L_AMEV1.1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Danger Property | {f,f,f,f} | 0 | 0 | {f} | reverse | Normal | Danger | >0* |  |  | 150 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | AMEV1.1
Operational Announcements
a413 | 34b26c5f-56fa-4256-b5aa-173b9c8978d7 | BI_BB_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Ready for operation | {f,f,f,f} | 0 | 0 | {f} | reverse | Ready | Not Ready |  | >0* |  | 300 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a414 | c6995422-eac8-45df-b3fb-afbac00c6853 | BI_BM_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Operating message | {f,f,f,f} | 0 | 0 | {f} | normal | Off | On |  | >0* | [8 empty] | {f}
a415 | ef45dc69-79ed-40d6-9833-2e93f671c10e | BI_BM_AS_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Operating message level "x" | {f,f,f,f} | 0 | 0 | {f} | normal | --- | Level "x" |  | >0* | [8 empty] | {f}
a416 | fdf9079c-a27f-47ee-aa67-0647efdf41cf | BI_BM_AFR_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Operating message | {f,f,f,f} | 0 | 0 | {f} |  | Off | Release |  | >0* | [8 empty] | {f}
a417 | 73feda32-622c-4e71-ad43-54b7c557c90b | BI_BM_AF_AMEV1.1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Operating message requested | {f,f,f,f} | 0 | 0 | {f} | normal | Off | Requested |  | >0* | [8 empty] | {f} |  |  |  |  | AMEV1.1
a418
a419 | 835f3b2c-90d1-4d5d-b272-568ab1bedca9 | BI_BM_GOL_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Operating message | {f,f,f,f} | 0 | 0 | {f} |  | Gas | Oil |  | >0* | [8 empty] | {f}
a420 | d2f6a37a-183f-417e-bac3-d61ebcd71634 | BI_BM_HKL_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Operating message | {f,f,f,f} | 0 | 0 | {f} |  | Heat | Cool |  | >0* | [8 empty] | {f}
a421 | 156709d2-acea-426d-8857-a098e0797df1 | BI_BM_LFN_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Operating message | {f,f,f,f} | 0 | 0 | {f} |  | Local | Remote |  | >0* | [8 empty] | {f}
a422 | 35d06169-858b-452a-bfd5-b19e3a9d33d1 | BI_BM_LRE_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Operating message | {f,f,f,f} | 0 | 0 | {f} |  | Left | Right |  | >0* | [8 empty] | {f}
a423 | 9b46266a-f9d5-42e3-a0a0-8f6672132276 | BI_BM_NAN_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Operating message | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Abnormal |  | >0* | [8 empty] | {f}
a424 | 134c04c7-d86a-4f82-9e99-24d793b739c2 | BI_BM_NU_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Operating message | {f,f,f,f} | 0 | 0 | {f} |  | Network A | Network B |  | >0* | [8 empty] | {f}
a425
a426 | b258cd2f-5b9f-429b-87cd-b144a6224d38 | BI_BM_NLA_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Operating message | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Busy |  | >0* | [8 empty] | {f}
a427 | 3c7fb6c1-f54a-44c8-a3c5-9f2ebb4e5fff | BI_BM_NOT_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Operating message | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Emergency |  | >0* | [8 empty] | {f}
a428 | f1f1d8cc-ed03-4330-92bc-ecf1e87362f1 | BI_BM_NRZ_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Operating message | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Reduced |  | >0* | [8 empty] | {f}
a429 | 9da3efd2-ae36-4e55-99f0-17503ade45d8 | BI_BM_NSP_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Operating message | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Locked |  | >0* | [8 empty] | {f}
a430 | f30af656-7cb4-4520-89ac-de6b3c144ce5 | BI_BM_NTG_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Operating message | {f,f,f,f} | 0 | 0 | {f} |  | Reduced | Comfort |  | >0* | [8 empty] | {f}
a431 | c40cf18b-2fce-4277-8495-4613b6a75524 | BI_BM_PA_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Operating message | {f,f,f,f} | 0 | 0 | {f} |  | --- | Open |  | >0* | [8 empty] | {f}
a432 | 5f7b30dd-3c92-43f2-8e3d-eaabc11a1cc4 | BI_BM_PAK_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Operating message | {f,f,f,f} | 0 | 0 | {f} |  | Passive | Active |  | >0* | [8 empty] | {f}
a433 | 976eb7de-b646-4811-9c8a-e655988cce26 | BI_BM_PZ_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Operating message | {f,f,f,f} | 0 | 0 | {f} |  | --- | Closed |  | >0* | [8 empty] | {f}
a434 | ce00fdac-1947-4906-8d9a-8577a0dd3827 | BI_BM_SEP_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Operating message | {f,f,f,f} | 0 | 0 | {f} |  | Start Position | End Position |  | >0* | [8 empty] | {f}
a435 | 267ef0fe-2efb-4578-8523-9fff993b257b | BI_BM_VHO_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Operating message | {f,f,f,f} | 0 | 0 | {f} |  | Normal | High |  | >0* | [8 empty] | {f}
a436 | 12783c14-be54-4f1d-b883-1abfeee9f37d | BI_BM_VTI_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Operating message | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Low |  | >0* | [8 empty] | {f}
a437 | dbb832e7-50f8-4f58-a1dd-58561b1060c6 | BI_BM_VZH_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Operating message | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Too High |  | >0* | [8 empty] | {f}
a438 | 39d1a987-6e50-4ba4-845f-145651b37579 | BI_BM_VZT_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Operating message | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Too Low |  | >0* | [8 empty] | {f}
a439 | 903c18a6-631f-41a0-96f1-db766d9d4c70 | BI_BM_WSO_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Operating message | {f,f,f,f} | 0 | 0 | {f} |  | Winter | Summer |  | >0* | [8 empty] | {f}
a440 | 4850c7d3-569f-4c9b-84c4-45d80db90147 | BI_BM_ZOF_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Operating message | {f,f,f,f} | 0 | 0 | {f} |  | Closed | Open |  | >0* | [8 empty] | {f}
a441
Feedback
a442 | c8bb6588-f7e3-4d4b-946e-5cf5e777a236 | BI_RM_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Feedback | {f,f,f,f} | 0 | 0 | {f} | normal | Closed | Open |  | >0* | [8 empty] | {f}
a443 | 9be71529-9e12-4477-bbad-74108f2f72bc | BI_RM_A_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Feedback Open | {f,f,f,f} | 0 | 0 | {f} | normal | Passive | Open |  | >0* | [8 empty] | {f}
a444 | 9af4e857-8a13-4a59-8884-77885254dca2 | BI_RM_Z_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Feedback Closed | {f,f,f,f} | 0 | 0 | {f} | normal | Passive | Closed |  | >0* | [8 empty] | {f}
a445 | 33fbb59d-0a40-4731-925a-b9672648200e | BI_RM_E_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Feedback On | {f,f,f,f} | 0 | 0 | {f} | normal | Passive | On |  | >0* | [8 empty] | {f}
a446 | e392203e-5fe1-4715-9e54-631941bb4a02 | BI_RM_S_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Feedback Off | {f,f,f,f} | 0 | 0 | {f} | normal | Passive | Off |  | >0* | [8 empty] | {f}
a447 | b084463a-fe50-481b-90b4-bce1d2628a07 | BI_RM_AK_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Feedback | {f,f,f,f} | 0 | 0 | {f} | normal | Off | On |  | >0* | [8 empty] | {f}
a448 | b28faa46-7717-4e7b-93a8-c982604bd99e | BI_RM_NJ_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Feedback | {f,f,f,f} | 0 | 0 | {f} | normal | No | Yes |  | >0* | [8 empty] | {f}
a449 | 8707a872-a167-4363-ba85-0d75b0815f3e | BI_RM_IO_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Feedback OK | {f,f,f,f} | 0 | 0 | {f} | normal | All Right | Deviation |  | >0* | [8 empty] | {f}
a450 | 40a81211-2cfa-4c3c-9775-a80f4e9dca47 | BI_PAE_AMEV1 |  | X |  | X | X | 1.1.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Feedback Presence | {f,f,f,f} | 0 | 0 | {f} | normal | No Presence | Presence |  | >0* | [8 empty] | {f}
a451 | dd2680c0-1ccc-4ac9-a10a-4efe86c76043 | BI_ENT_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Unlocking | {f,f,f,f} | 0 | 0 | {f} | normal | Inactive | Active |  | >0* | 0 | 500 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a452 | c66d9b08-d2fb-4543-8491-acf5474c2967 | BI_VRR_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Locking | {f,f,f,f} | 0 | 0 | {f} | normal | Inactive | Active |  | >0* | 0 | 600 | active | {t,t,t} | Event | * | * | *** | {t} |  |  | 1
Maintenance/Manual Messages
a453 | f4894ea4-2d89-4aa0-9195-6e04dd467467 | BI_WM_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Maintenance message | {f,f,f,f} | 0 | 0 | {f} | normal | Normal | Maintenance | >0* |  |  | 400 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a454 | 0d36d9ae-4e64-4c79-8e15-7f6361146ddb | BI_WM_FI_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Maintenance message Filter | {f,f,f,f} | 0 | 0 | {f} | normal | Normal | Active | >0* |  |  | 425 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a455 | 2af0c66a-b562-42f7-93b6-1e3954231498 | BI_WM_REP_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Repair switch | {f,f,f,f} | 0 | 0 | {f} | normal | Inactive | Active | >0* |  |  | 400 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a456 | 102d3257-a732-4a3e-99e0-7d8988cdc658 | BI_RVM_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Revision message | {f,f,f,f} | 0 | 0 | {f} | normal | Inactive | Revision | >0* |  |  | 450 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
a457 | d608082b-79b9-4098-b1a2-db2738a012d1 | BI_HD_AMEV1 |  | X | X | X | X | 1.1.2; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Local override message | {f,f,f,f} | 0 | 0 | {f} | normal | Auto | Hand | >0* |  |  | 500 | active | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1
|  | * B (Builder/Operator), P (Planning), X (Executing Company) | [6 empty] | Default value (parameterization) and test value | [9 empty] | * Can be used for testing in the 1:1 test | [6 empty] | *** Implementation according to Chapter 4.5
[9 empty] | Test value (internally generated value) | [16 empty] | [*] Suppress alarms when the system is switched off

## 8.4 BO_BV
ObjSort + LfdNr | UUID | Objekt-Template- Kennung | Kommentar | GA-FL Einträge (1.1.4) | GA-FL Einträge (1.2.2) | GA-FL Einträge (2.2.1) | GA-FL Einträge (2.2.41) | GA-FL Einträge (3.1.1) | GA-FL Einträge (3.1.3) | GA-FL Einträge (Abschnitte/Spalten) | Object_Name | Description | Verwendung | Status_Flags | Event_State | Reliability | Out_Of_Service | Polarity (nur BO) | Inactive_Text | Active_Text | Change_Of_State_Count | Elapsed_Active_Time | Mininum_Off_Time | Mininum_On_Time | Relinquish_Default | Time_Delay | Notification_Class | Alarm_Value (nur BV) | Feedback_Value (nur BO) | Event_Enable | Notify_Type | Event_Time_Stamps | Event_Message_Texts | Event_Message_Texts_Config | Event_Detection_Enable | Event_Algorithm_Inhibit | Event_Algorithm_Inhibit_Ref | Time_Delay_Normal | Reliability_Evaluation_Inhibit | Current_Command_Priority | Letztmalige Änderung in Version
|  | PropSort | [8 empty] | a11 | a12 | [5 empty] | b12 | b13 | b14 |  |  | b43 | b44 | b16 | c43 | c11 | c16 | c19 | c12 | c13 |  |  | c14 | c15 | c41 | c42 | c44
|  | Conformance Code | [8 empty] | R | W |  | R | R | W1 | W | W | W | W | R0 | R0 | W | W | W | W | W | W | R | W | W | R | R | W | W | RA | RA | W | RX¦O | R22
|  | Grundlegende Vorgabe * | [8 empty] | B * | B | [5 empty] | B | B | B |  |  | P | P | B | P | B | B | B | B | B |  |  | B | B | P | P | P
|  | Detailierte Festlegung * | [8 empty] | P * | P | [5 empty] | P | P | P |  |  | P | P | P | P | P | P | U | P | P |  |  | P | P | P | P | P
|  | Umsetzung * | [8 empty] | U * | U |  | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U |  |  | U | U | U | U | U | U | U
|  | Vorgabewert (Parametrierung) | [8 empty] | ja | ja |  | nein | nein | nein | nein | nein | ja | ja | nein | nein | ja | ja | ja | ja | ja | ja | nein | ja | ja | nein | nein | ja | ja | nein | nein | ja | nein | nein
Schaltbefehl (BO)
a501 | dd66fddc-769c-45e1-a7f7-3251dede24bc | BO_SB_AMEV1 |  | X |  |  | X | X | X | 1.1.4; 2.2.41; 3.1.1; 3.1.3 | [BAS] | [Description] | Schaltbefehl | {f,f,f,f} | 0 | 0 | {f} |  | Aus | Ein | >0* | >0* |  |  | inactive | [60]¹ | 300¹ |  |  | {t,t,t}¹ | Alarm¹ | *¹ | *¹ | ***¹ | {t/f}¹ |  |  | 1¹ |  | >8
a502 | 68ad0558-2015-4275-8472-0fe483cbd018 | BO_SBA_AMEV1 |  | X |  |  | X | X | X | 1.1.4; 2.2.41; 3.1.1; 3.1.3 | [BAS] | [Description] | Schaltbefehl auf | {f,f,f,f} | 0 | 0 | {f} |  | Passiv | Auf | >0* | >0* |  |  | inactive | [60]¹ | 300¹ |  |  | {t,t,t}¹ | Alarm¹ | *¹ | *¹ | ***¹ | {t/f}¹ |  |  | 1¹ |  | >8
a503 | af923912-1487-4c87-a8b1-312846be21d6 | BO_SBZ_AMEV1 |  | X |  |  | X | X | X | 1.1.4; 2.2.41; 3.1.1; 3.1.3 | [BAS] | [Description] | Schaltbefehl zu | {f,f,f,f} | 0 | 0 | {f} |  | Passiv | Zu | >0* | >0* |  |  | inactive | [60]¹ | 300¹ |  |  | {t,t,t}¹ | Alarm¹ | *¹ | *¹ | ***¹ | {t/f}¹ |  |  | 1¹ |  | >8
a504 | 4a2c8401-28e3-4b5a-a396-0f0189c462e0 | BO_SB_AS_AMEV1 |  | X |  |  | X | X | X | 1.1.4; 2.2.41; 3.1.1; 3.1.3 | [BAS] | [Description] | Schaltbefehl Stufe "x" | {f,f,f,f} | 0 | 0 | {f} |  | Aus | Stufe "X" | >0* | >0* |  |  | inactive | [60]¹ | 300¹ |  |  | {t,t,t}¹ | Alarm¹ | *¹ | *¹ | ***¹ | {t/f}¹ |  |  | 1¹ |  | >8
a505 | 512eee31-d962-4f62-aaca-fe874dee66b6 | BO_SB_KL_AMEV1 |  | X |  |  | X | X | X | 1.1.4; 2.2.41; 3.1.1; 3.1.3 | [BAS] | [Description] | Schaltbefehl | {f,f,f,f} | 0 | 0 | {f} |  | Auf | Zu | >0* | >0* |  |  | inactive | [60]¹ | 300¹ |  |  | {t,t,t}¹ | Alarm¹ | *¹ | *¹ | ***¹ | {t/f}¹ |  |  | 1¹ |  | >8
a506 | a3515c8e-8960-4ed6-9823-2fbc2385b551 | BO_SB_ZOF_AMEV1 |  | X |  |  | X | X | X | 1.1.4; 2.2.41; 3.1.1; 3.1.3 | [BAS] | [Description] | Schaltbefehl | {f,f,f,f} | 0 | 0 | {f} |  | Geschlossen | Offen | >0* | >0* |  |  | inactive | [60]¹ | 300¹ |  |  | {t,t,t}¹ | Alarm¹ | *¹ | *¹ | ***¹ | {t/f}¹ |  |  | 1¹ |  | >8
a507 | 6a7f78c2-c2d6-4358-b325-1972796ad5a1 | BO_BM_AMEV1 | an anderes Gerät | X |  |  | X | X | X | 1.1.4; 2.2.41; 3.1.1; 3.1.3 | [BAS] | [Description] | Betriebsmeldung | {f,f,f,f} | 0 | 0 | {f} |  | Inaktiv | Aktiv | >0* | >0* |  |  | inactive | [60]¹ | 150/200¹ |  |  | {t,t,t}¹ | Alarm¹ | *¹ | *¹ | ***¹ | {t/f}¹ |  |  | 1¹ |  | >8
a508 | 72134349-21d7-4862-bd31-c6caf646312c | BO_FG_AMEV1 |  | X |  |  | X | X | X | 1.1.4; 2.2.41; 3.1.1; 3.1.3 | [BAS] | [Description] | Freigabe | {f,f,f,f} | 0 | 0 | {f} |  | Gesperrt | Freigegeben | >0* | >0* |  |  | inactive | [60]¹ | 300¹ |  |  | {t,t,t}¹ | Alarm¹ | *¹ | *¹ | ***¹ | {t/f}¹ |  |  | 1¹ |  | >8
a509 | 38b5e700-105a-41ff-a3ba-a3afd661f384 | BO_FG_SI_AMEV1 | z.B. für Laufzeittest BSK | X |  | X |  | X | X | 1.1.4; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Freigabe Laufzeittest | {f,f,f,f} | 0 | 0 | {f} |  | Gesperrt | Freigegeben | >0* | >0* |  |  | inactive | [600] | 100 |  |  | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a510 | 0c26be3c-8322-4435-8410-20688929fb5d | BO_SB_VDR_AMEV1 |  | X |  |  | X | X | X | 1.1.4; 2.2.41; 3.1.1; 3.1.3 | [BAS] | [Description] | Schaltbefehl | {f,f,f,f} | 0 | 0 | {f} |  | Aus | Ein | >0* | >0* | [300] | [60] | inactive | [60]¹ | 300¹ |  |  | {t,t,t}¹ | Alarm¹ | *¹ | *¹ | ***¹ | {t/f}¹ |  |  | 1¹ |  | >8
Schaltbefehl (BV)
a601 | b5ef28d6-0dcf-417d-a279-0d202b06ba41 | BV_SB_AAF_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Schaltbefehl | {f,f,f,f} | 0 | 0 | {f} |  | Ab | Auf |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a602 | af44d66f-5430-495e-8433-cf1902852261 | BV_SB_STT_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Schaltbefehl | {f,f,f,f} | 0 | 0 | {f} |  | Passiv | Start |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a603 | 4ca426aa-5a73-4d7e-be43-cf0a4f3ca0cb | BV_SB_STP_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Schaltbefehl | {f,f,f,f} | 0 | 0 | {f} |  | Passiv | Stopp |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a604 | 617d4224-d121-4408-ad4f-b2378987e335 | BV_SB_ZVO_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Schaltbefehl | {f,f,f,f} | 0 | 0 | {f} |  | Zurück | Vor |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a605 | c8ac53bb-37b6-48f2-943e-198e6139ccf7 | BV_SB_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Schaltbefehl | {f,f,f,f} | 0 | 0 | {f} |  | Aus | Ein |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a606 | 1c5dce0f-db67-423b-8b4c-1534c290b154 | BV_SB_GM_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Schaltbefehl Gefahrmeldung | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Gefahr |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a607 | cb14b768-511b-4b40-b4d5-08e7158dc0b1 | BV_SB_GM_BSK_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Schaltbefehl Gefahrmeldung | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Gefallen |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a608 | 33f64dbb-1424-44f5-bef8-8e050589feb4 | BV_SB_AM_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Schaltbefehl Alarmmeldung | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Alarm |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a609 | db588d63-4077-4725-b620-192bc2245cbd | BV_SB_SM_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Schaltbefehl Störmeldung | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Störung |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a610 | 393f5c05-2564-46ac-b480-e3fc49526400 | BV_SB_BB_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Schaltbefehl Betriebsbereit | {f,f,f,f} | 0 | 0 | {f} |  | Nicht bereit | Bereit |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a611 | 59309b06-5752-405c-b887-ca110c5434e8 | BV_SB_AFR_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Schaltbefehl | {f,f,f,f} | 0 | 0 | {f} |  | Aus | Freigabe |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a612 | 35c7de11-075b-472e-a0e3-cb18b5740251 | BV_SB_HKL_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Schaltbefehl | {f,f,f,f} | 0 | 0 | {f} |  | Heizen | Kühlen |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a613 | 9527e43e-b9d4-4aa9-826f-af969d6955dd | BV_SB_NOT_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Schaltbefehl | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Notbetrieb |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a614 | 71a5fd4e-8353-4d38-aa08-bb0c73120787 | BV_SB_NSP_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Schaltbefehl | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Gesperrt |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a615 | 36c7a3d8-2b00-44a9-8e6c-dfe9838e5b24 | BV_SB_WSO_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Schaltbefehl | {f,f,f,f} | 0 | 0 | {f} |  | Winter | Sommer |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a616 | c3fdc577-db40-4d50-b277-bb49cd5bb6d5 | BV_SB_ZAF_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Schaltbefehl | {f,f,f,f} | 0 | 0 | {f} |  | Zu | Auf |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a617 | e8c2c566-cf28-401e-b6cf-314d6f406d0f | BV_SB_A_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Schaltbefehl | {f,f,f,f} | 0 | 0 | {f} |  | Passiv | Auf |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a618 | 8a589084-02aa-4ca0-9836-0e9022133d63 | BV_SB_Z_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Schaltbefehl | {f,f,f,f} | 0 | 0 | {f} |  | Passiv | Zu |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a619 | 1ede4c7a-254d-4a76-97c8-21f8ec2ab1b1 | BV_ENT_AMEV1 |  |  | X | X |  | X | X | 1.1.4; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Entriegelung UBE | {f,f,f,f} | 0 | 0 | {f} |  | Inaktiv | Aktiv |  |  |  |  | inactive | 0 | 500 | active |  | {t,t,t} | Event | * | * | *** | {t} |  |  |  |  | >8
a620 | bcc42a9f-94ca-4282-a469-c9c7cd52c428 | BV_SB_R_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Reduziert | {f,f,f,f} | 0 | 0 | {f} |  | Inaktiv | Reduzierung |  |  |  |  | inactive | [9 empty] | {t} |  |  |  |  | >8
Anforderung (BV)
a621 | cfb49e8a-42e1-436c-ba5d-fee44aa0322c | BV_AF_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Anforderung | {f,f,f,f} | 0 | 0 | {f} |  | Aus | Ein |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a622 | c1df6fa5-f111-4b72-92ea-6f26e263101f | BV_AF_TH_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Anforderung | {f,f,f,f} | 0 | 0 | {f} |  | Passiv | Heizen |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a623 | e22f32e0-c54e-47b8-b010-5dda9726d389 | BV_AF_TK_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Anforderung | {f,f,f,f} | 0 | 0 | {f} |  | Passiv | Kühlen |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a624 | 6f465192-06d1-4841-a019-cdff44217111 | BV_AF_BEL_V_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Anforderung Beleuchtung | {f,f,f,f} | 0 | 0 | {f} |  | Aus | Ein Beleuchtung |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a625 | 72e2f4a6-e01d-4bbb-aa8e-e596fa567891 | BV_AF_BEL_R_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Anforderung Beleuchtung | {f,f,f,f} | 0 | 0 | {f} |  | Aus | Reduzierte Beleuchtung |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a626 | a60d187a-5727-4d73-9815-55f2aeb3c22f | BV_AF_SON_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Anforderung Sonnenschutz | {f,f,f,f} | 0 | 0 | {f} |  | Aus | Ein Sonnenschutz |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a627 | b37ffd36-971b-4fb9-a0f5-c4872588d901 | BV_AF_TMP_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Anforderung Temperierung | {f,f,f,f} | 0 | 0 | {f} |  | Aus | Ein Temperierung |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a628 | 09453584-aad5-4321-8ab4-682f41349274 | BV_AF_RLT_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Anforderung Belüftung | {f,f,f,f} | 0 | 0 | {f} |  | Aus | Ein Belüftung |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
Meldung kommunikativ
a629 | 9fd7e048-62b9-4f9a-81c6-720177bd84cc | BV_BM_AMEV1 | kommunikativ |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Betriebsmeldung | {f,f,f,f} | 0 | 0 | {f} |  | Aus | Ein |  | >0* | [12 empty] | {f} |  |  |  |  | >8
a630 | 450dcdfc-6a8b-4e1f-95ae-d239f1a4a856 | BV_BM_NOP_AMEV1 | kommunikativ |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Betriebsmeldung | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Optimieren |  | >0* | [12 empty] | {f} |  |  |  |  | >8
a631 | ef3afdbe-9697-4440-bafa-6e809dfaa083 | BV_RM_AMEV1 | kommunikativ |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Rückmeldung | {f,f,f,f} | 0 | 0 | {f} |  | Inaktiv | Aktiv | [14 empty] | {f} |  |  |  |  | >8
a632 | 367db8e6-5cc9-4fc7-b368-86f5d6e2a616 | BV_RM_JN_AMEV1 | kommunikativ |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Rückmeldung | {f,f,f,f} | 0 | 0 | {f} |  | Nein | Ja | [14 empty] | {f} |  |  |  |  | >8
a633 | 6b118880-efda-4d8c-90ae-8233c33ca94b | BV_SM_AMEV1 | kommunikativ |  | X | X |  | X | X | 1.2.2; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Störmeldung | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Störung | >0* | [5 empty] | 300 | active |  | {t,t,t} | Alarm | * | * | *** | {t} |  |  |  |  | >8
a634 | c5cfcaa4-ed88-4d8a-afde-2a942f204654 | BV_SM_NAF_AMEV1 | Kommunikation ausgefallen |  | X | X |  | X | X | 1.2.2; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Störmeldung | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Ausgefallen | >0* | [5 empty] | 300 | active |  | {t,t,t} | Alarm | * | * | *** | {t} |  |  |  |  | >8
a635 | df711e2c-56b8-4f91-819b-3657654b6689 | BV_SM_AK_AMEV1 |  |  | X |  | X | X | X | 1.2.2; 2.2.41; 3.1.1; 3.1.3 | [BAS] | [Description] | Ausführkontrolle | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Anormal | >0* | [5 empty] | 300 | active |  | {t,t,t} | Alarm | * | * | *** | {t} |  |  |  |  | >8
a636 | 45b4be2e-3262-46ac-b9d8-6bc710db996a | BV_SM_NOF_AMEV1 |  |  | X | X |  | X | X | 1.2.2; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Störmeldung | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Offline | >0* | [5 empty] | 600 | active |  | {t,t,t} | Alarm | * | * | *** | {t} |  |  |  |  | >8
a637 | 443aeb91-26d7-4b19-9116-00d88b83da7f | BV_SM_LU_IH_AMEV1 |  |  | X | X |  | X | X | 1.2.2; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Störmeldung | {f,f,f,f} | 0 | 0 | {f} |  | Lufströmung | kein Luftströmung | >0* |  |  |  |  | [60] | 200 | active |  | {t,t,t} | Alarm | * | * | *** | {t} | [**] | [**] |  |  | >8
a638 | 839c00d1-d282-4a19-9a80-f339ac8215c3 | BV_WM_BZ_AMEV1 |  |  | X | X |  | X | X | 1.2.2; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Wartungsmeldung Betriebsstunden | {f,f,f,f} | 0 | 0 | {f} |  | Inaktiv | Aktiv | >0* | [5 empty] | 400 | active |  | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
Meldung Status (Anlagenschalter)
a639 | becf5e9e-cf74-4b70-b278-21cdaa2c0057 | BV_STA_ADZM_AMEV1 |  |  | X | X |  | X | X | 1.2.2; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} |  | Hand-Aus | Drehzahl-Vorgabe | >0* | [5 empty] | 500 | active |  | {t,t,t} | Alarm | * | * | *** | {t} |  |  |  |  | >8
a640 | 5b4952dc-be53-4f95-8ece-0c33b35003db | BV_STA_P2M_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} |  | Pumpe 1 | Pumpe 2 |  | >0* | [12 empty] | {t} |  |  |  |  | >8
a641 | 6233a058-1046-482e-88ea-5bad4a123bfe | BV_STA_E2M_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} |  | Erzeuger 1 | Erzeuger 2 |  | >0* | [12 empty] | {t} |  |  |  |  | >8
a642 | 188b0278-4ad5-4b3c-99e0-59a09992936c | BV_STA_E_AMEV1 | Beleuchtung |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} |  | Aus | Ein | [14 empty] | {f} |  |  |  |  | >8
|  | * B (Bauherr/Betreiber), P (GA-Planung), U (Ausführendes Unternehmen) | [8 empty] | Vorgabewert (Parametrierung) und Prüfwert | [9 empty] | [] => Default-Werte (Vorschlag) | [11 empty] | * Kann zur Prüfung beim 1:1 Test herangezogen werden
[11 empty] | Prüfwert (systemintern erzeugter Wert) | [9 empty] | 1 Nur wenn Ausführkontrolle über Intrinsic Alarming ausgeführt wird | [11 empty] | ** Alarmierung bei abgeschalteter Anlage unterdrücken
*** gemäß Kapitel 4.4 einrichten
ENGLISH VERSION (Draft)
ObjSort + No. | UUID | Object Template Identifier | Comment | BACS FL entries (1.1.4) | BACS FL entries (1.2.2) | BACS FL entries (2.2.1) | BACS FL entries (2.2.41) | BACS FL entries (3.1.1) | BACS FL entries (3.1.3) | BACS FL entries (sections/columns) | Object_Name | Description | Application | Status_Flags | Event_State | Reliability | Out_Of_Service | Polarity (only BO) | Inactive_Text | Active_Text | Change_Of_State_Count | Elapsed_Active_Time | Mininum_Off_Time | Mininum_On_Time | Relinquish_Default | Time_Delay | Notification_Class | Alarm_Value (only BV) | Feedback_Value (only BO) | Event_Enable | Notify_Type | Event_Time_Stamps | Event_Message_Texts | Event_Message_Texts_Config | Event_Detection_Enable | Event_Algorithm_Inhibit | Event_Algorithm_Inhibit_Ref | Time_Delay_Normal | Reliability_Evaluation_Inhibit | Current_Command_Priority | Last change in version
|  | PropSort | [8 empty] | a11 | a12 | [5 empty] | b12 | b13 | b14 |  |  | b43 | b44 | b16 | c43 | c11 | c16 | c19 | c12 | c13 |  |  | c14 | c15 | c41 | c42 | c44
|  | Conformance Code | [8 empty] | R | W |  | R | R | W1 | W | W | W | W | R0 | R0 | W | W | W | W | W | W | R | W | W | R | R | W | W | RA | RA | W | RX¦O | R22
|  | Basic spezification * | [8 empty] | B * | B | [5 empty] | B | B | B |  |  | P | P | B | P | B | B | B | B | B |  |  | B | B | P | P | P
|  | Detailed definition * | [8 empty] | P * | P | [5 empty] | P | P | P |  |  | P | P | P | P | P | P | X | P | P |  |  | P | P | P | P | P
|  | Implementation * | [8 empty] | X * | X |  | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X |  |  | X | X | X | X | X | X | X
|  | Default value (parameterization) | [8 empty] | yes | yes |  | no | no | no | no | no | yes | yes | no | no | yes | yes | yes | yes | yes | yes | no | yes | yes | no | no | yes | yes | no | no | yes | no | no
Switching Command (BO)
a501 | dd66fddc-769c-45e1-a7f7-3251dede24bc | BO_SB_AMEV1 |  | X |  |  | X | X | X | 1.1.4; 2.2.41; 3.1.1; 3.1.3 | [UAK] | [Description] | Switching command | {f,f,f,f} | 0 | 0 | {f} |  | Off | On | >0* | >0* |  |  | inactive | [60]¹ | 300¹ |  |  | {t,t,t}¹ | Alarm¹ | *¹ | *¹ | ***¹ | {t/f}¹ |  |  | 1¹ |  | >8
a502 | 68ad0558-2015-4275-8472-0fe483cbd018 | BO_SBA_AMEV1 |  | X |  |  | X | X | X | 1.1.4; 2.2.41; 3.1.1; 3.1.3 | [UAK] | [Description] | Switching command Open | {f,f,f,f} | 0 | 0 | {f} |  | Passive | Open | >0* | >0* |  |  | inactive | [60]¹ | 300¹ |  |  | {t,t,t}¹ | Alarm¹ | *¹ | *¹ | ***¹ | {t/f}¹ |  |  | 1¹ |  | >8
a503 | af923912-1487-4c87-a8b1-312846be21d6 | BO_SBZ_AMEV1 |  | X |  |  | X | X | X | 1.1.4; 2.2.41; 3.1.1; 3.1.3 | [UAK] | [Description] | Switching command Close | {f,f,f,f} | 0 | 0 | {f} |  | Passive | Closed | >0* | >0* |  |  | inactive | [60]¹ | 300¹ |  |  | {t,t,t}¹ | Alarm¹ | *¹ | *¹ | ***¹ | {t/f}¹ |  |  | 1¹ |  | >8
a504 | 4a2c8401-28e3-4b5a-a396-0f0189c462e0 | BO_SB_AS_AMEV1 |  | X |  |  | X | X | X | 1.1.4; 2.2.41; 3.1.1; 3.1.3 | [UAK] | [Description] | Switching command Level "x" | {f,f,f,f} | 0 | 0 | {f} |  | Off | Level "X" | >0* | >0* |  |  | inactive | [60]¹ | 300¹ |  |  | {t,t,t}¹ | Alarm¹ | *¹ | *¹ | ***¹ | {t/f}¹ |  |  | 1¹ |  | >8
a505 | 512eee31-d962-4f62-aaca-fe874dee66b6 | BO_SB_KL_AMEV1 |  | X |  |  | X | X | X | 1.1.4; 2.2.41; 3.1.1; 3.1.3 | [UAK] | [Description] | Switching command | {f,f,f,f} | 0 | 0 | {f} |  | Open | Closed | >0* | >0* |  |  | inactive | [60]¹ | 300¹ |  |  | {t,t,t}¹ | Alarm¹ | *¹ | *¹ | ***¹ | {t/f}¹ |  |  | 1¹ |  | >8
a506 | a3515c8e-8960-4ed6-9823-2fbc2385b551 | BO_SB_ZOF_AMEV1 |  | X |  |  | X | X | X | 1.1.4; 2.2.41; 3.1.1; 3.1.3 | [UAK] | [Description] | Switching command | {f,f,f,f} | 0 | 0 | {f} |  | Closed | Open | >0* | >0* |  |  | inactive | [60]¹ | 300¹ |  |  | {t,t,t}¹ | Alarm¹ | *¹ | *¹ | ***¹ | {t/f}¹ |  |  | 1¹ |  | >8
a507 | 6a7f78c2-c2d6-4358-b325-1972796ad5a1 | BO_BM_AMEV1 | to another device | X |  |  | X | X | X | 1.1.4; 2.2.41; 3.1.1; 3.1.3 | [UAK] | [Description] | Operating message | {f,f,f,f} | 0 | 0 | {f} |  | Inactive | Active | >0* | >0* |  |  | inactive | [60]¹ | 150/200¹ |  |  | {t,t,t}¹ | Alarm¹ | *¹ | *¹ | ***¹ | {t/f}¹ |  |  | 1¹ |  | >8
a508 | 72134349-21d7-4862-bd31-c6caf646312c | BO_FG_AMEV1 |  | X |  |  | X | X | X | 1.1.4; 2.2.41; 3.1.1; 3.1.3 | [UAK] | [Description] | Release | {f,f,f,f} | 0 | 0 | {f} |  | Locked | Released | >0* | >0* |  |  | inactive | [60]¹ | 300¹ |  |  | {t,t,t}¹ | Alarm¹ | *¹ | *¹ | ***¹ | {t/f}¹ |  |  | 1¹ |  | >8
a509 | 38b5e700-105a-41ff-a3ba-a3afd661f384 | BO_FG_SI_AMEV1 | e.g. for runtime test fire damper | X |  | X |  | X | X | 1.1.4; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Release runtime test | {f,f,f,f} | 0 | 0 | {f} |  | Locked | Released | >0* | >0* |  |  | inactive | [600] | 100 |  |  | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
a510 | 0c26be3c-8322-4435-8410-20688929fb5d | BO_SB_VDR_AMEV1 |  | X |  |  | X | X | X | 1.1.4; 2.2.41; 3.1.1; 3.1.3 | [UAK] | [Description] | Switching command | {f,f,f,f} | 0 | 0 | {f} |  | Off | On | >0* | >0* | [300] | [60] | inactive | [60]¹ | 300¹ |  |  | {t,t,t}¹ | Alarm¹ | *¹ | *¹ | ***¹ | {t/f}¹ |  |  | 1¹ |  | >8
Switching Command (BV)
a601 | b5ef28d6-0dcf-417d-a279-0d202b06ba41 | BV_SB_AAF_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Switching command | {f,f,f,f} | 0 | 0 | {f} |  | Down | Up |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a602 | af44d66f-5430-495e-8433-cf1902852261 | BV_SB_STT_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Switching command | {f,f,f,f} | 0 | 0 | {f} |  | Passive | Start |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a603 | 4ca426aa-5a73-4d7e-be43-cf0a4f3ca0cb | BV_SB_STP_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Switching command | {f,f,f,f} | 0 | 0 | {f} |  | Passive | Stop |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a604 | 617d4224-d121-4408-ad4f-b2378987e335 | BV_SB_ZVO_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Switching command | {f,f,f,f} | 0 | 0 | {f} |  | Back | Foreward |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a605 | c8ac53bb-37b6-48f2-943e-198e6139ccf7 | BV_SB_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Switching command | {f,f,f,f} | 0 | 0 | {f} |  | Off | On |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a606 | 1c5dce0f-db67-423b-8b4c-1534c290b154 | BV_SB_GM_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Switching command Hazard alarm | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Danger |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a607 | cb14b768-511b-4b40-b4d5-08e7158dc0b1 | BV_SB_GM_BSK_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Switching command Hazard alarm | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Fallen |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a608 | 33f64dbb-1424-44f5-bef8-8e050589feb4 | BV_SB_AM_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Switching command Alarm message | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Alarm |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a609 | db588d63-4077-4725-b620-192bc2245cbd | BV_SB_SM_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Switching command Fault message | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Fault |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a610 | 393f5c05-2564-46ac-b480-e3fc49526400 | BV_SB_BB_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Switching command Ready for Operation | {f,f,f,f} | 0 | 0 | {f} |  | Not Ready | Ready |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a611 | 59309b06-5752-405c-b887-ca110c5434e8 | BV_SB_AFR_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Switching command | {f,f,f,f} | 0 | 0 | {f} |  | Off | Release |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a612 | 35c7de11-075b-472e-a0e3-cb18b5740251 | BV_SB_HKL_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Switching command | {f,f,f,f} | 0 | 0 | {f} |  | Heat | Cool |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a613 | 9527e43e-b9d4-4aa9-826f-af969d6955dd | BV_SB_NOT_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Switching command | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Emergency |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a614 | 71a5fd4e-8353-4d38-aa08-bb0c73120787 | BV_SB_NSP_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Switching command | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Locked |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a615 | 36c7a3d8-2b00-44a9-8e6c-dfe9838e5b24 | BV_SB_WSO_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Switching command | {f,f,f,f} | 0 | 0 | {f} |  | Winter | Summer |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a616 | c3fdc577-db40-4d50-b277-bb49cd5bb6d5 | BV_SB_ZAF_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Switching command | {f,f,f,f} | 0 | 0 | {f} |  | Closed | Open |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a617 | e8c2c566-cf28-401e-b6cf-314d6f406d0f | BV_SB_A_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Switching command | {f,f,f,f} | 0 | 0 | {f} |  | Passive | Open |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a618 | 8a589084-02aa-4ca0-9836-0e9022133d63 | BV_SB_Z_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Switching command | {f,f,f,f} | 0 | 0 | {f} |  | Passive | Closed |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a619 | 1ede4c7a-254d-4a76-97c8-21f8ec2ab1b1 | BV_ENT_AMEV1 |  |  | X |  |  | X | X | 1.1.4; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Unlocking UOU | {f,f,f,f} | 0 | 0 | {f} |  | Inactive | Active |  |  |  |  | inactive | 0 | 500 | active |  | {t,t,t} | Event | * | * | *** | {t} |  |  |  |  | >8
a620 | bcc42a9f-94ca-4282-a469-c9c7cd52c428 | BV_SB_R_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Reduced | {f,f,f,f} | 0 | 0 | {f} |  | Inactive | Reduction |  |  |  |  | inactive | [9 empty] | {t} |  |  |  |  | >8
Requirement (BV)
a621 | cfb49e8a-42e1-436c-ba5d-fee44aa0322c | BV_AF_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Requirement | {f,f,f,f} | 0 | 0 | {f} |  | Off | On |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a622 | c1df6fa5-f111-4b72-92ea-6f26e263101f | BV_AF_TH_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Requirement | {f,f,f,f} | 0 | 0 | {f} |  | Passive | Heat |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a623 | e22f32e0-c54e-47b8-b010-5dda9726d389 | BV_AF_TK_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Requirement | {f,f,f,f} | 0 | 0 | {f} |  | Passive | Cool |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a624 | 6f465192-06d1-4841-a019-cdff44217111 | BV_AF_BEL_V_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Requirement Lighting | {f,f,f,f} | 0 | 0 | {f} |  | Off | On Lighting |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a625 | 72e2f4a6-e01d-4bbb-aa8e-e596fa567891 | BV_AF_BEL_R_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Requirement Lighting | {f,f,f,f} | 0 | 0 | {f} |  | Off | On Lighting Reduced |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a626 | a60d187a-5727-4d73-9815-55f2aeb3c22f | BV_AF_SON_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Requirement Sun protection | {f,f,f,f} | 0 | 0 | {f} |  | Off | On Sunshade |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a627 | b37ffd36-971b-4fb9-a0f5-c4872588d901 | BV_AF_TMP_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Requirement Temperature control | {f,f,f,f} | 0 | 0 | {f} |  | Off | On Temperature Control |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
a628 | 09453584-aad5-4321-8ab4-682f41349274 | BV_AF_RLT_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Requirement Ventilation | {f,f,f,f} | 0 | 0 | {f} |  | Off | On Ventilation |  |  |  |  | inactive | [9 empty] | {f} |  |  |  |  | >8
Message communicative
a629 | 9fd7e048-62b9-4f9a-81c6-720177bd84cc | BV_BM_AMEV1 | communicative |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Operating message | {f,f,f,f} | 0 | 0 | {f} |  | Off | On |  | >0* | [12 empty] | {f} |  |  |  |  | >8
a630 | 450dcdfc-6a8b-4e1f-95ae-d239f1a4a856 | BV_BM_NOP_AMEV1 | communicative |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Operating message | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Optimize |  | >0* | [12 empty] | {f} |  |  |  |  | >8
a631 | ef3afdbe-9697-4440-bafa-6e809dfaa083 | BV_RM_AMEV1 | communicative |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Feedback | {f,f,f,f} | 0 | 0 | {f} |  | Inactive | Active | [14 empty] | {f} |  |  |  |  | >8
a632 | 367db8e6-5cc9-4fc7-b368-86f5d6e2a616 | BV_RM_JN_AMEV1 | communicative |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Feedback | {f,f,f,f} | 0 | 0 | {f} |  | No | Yes | [14 empty] | {f} |  |  |  |  | >8
a633 | 6b118880-efda-4d8c-90ae-8233c33ca94b | BV_SM_AMEV1 | communicative |  | X | X |  | X | X | 1.2.2; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Fault message | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Fault | >0* | [5 empty] | 300 | active |  | {t,t,t} | Alarm | * | * | *** | {t} |  |  |  |  | >8
a634 | c5cfcaa4-ed88-4d8a-afde-2a942f204654 | BV_SM_NAF_AMEV1 | Failed communication |  | X | X |  | X | X | 1.2.2; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Fault message | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Out | >0* | [5 empty] | 300 | active |  | {t,t,t} | Alarm | * | * | *** | {t} |  |  |  |  | >8
a635 | df711e2c-56b8-4f91-819b-3657654b6689 | BV_SM_AK_AMEV1 |  |  | X |  | X | X | X | 1.2.2; 2.2.41; 3.1.1; 3.1.3 | [UAK] | [Description] | Execution Control | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Abnormal | >0* | [5 empty] | 300 | active |  | {t,t,t} | Alarm | * | * | *** | {t} |  |  |  |  | >8
a636 | 45b4be2e-3262-46ac-b9d8-6bc710db996a | BV_SM_NOF_AMEV1 |  |  | X | X |  | X | X | 1.2.2; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Fault message | {f,f,f,f} | 0 | 0 | {f} |  | Normal | Offline | >0* | [5 empty] | 600 | active |  | {t,t,t} | Alarm | * | * | *** | {t} |  |  |  |  | >8
a637 | 443aeb91-26d7-4b19-9116-00d88b83da7f | BV_SM_LU_IH_AMEV1 |  |  | X | X |  | X | X | 1.2.2; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Fault message | {f,f,f,f} | 0 | 0 | {f} |  | Air Flow | No Air Flow | >0* |  |  |  |  | [60] | 200 | active |  | {t,t,t} | Alarm | * | * | *** | {t} | [**] | [**] |  |  | >8
a638 | 839c00d1-d282-4a19-9a80-f339ac8215c3 | BV_WM_BZ_AMEV1 |  |  | X | X |  | X | X | 1.2.2; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Maintenance message Operating hours | {f,f,f,f} | 0 | 0 | {f} |  | Inactive | Active | >0* | [5 empty] | 400 | active |  | {t,t,t} | Alarm | * | * | *** | {t} |  |  | 1 |  | >8
Message Status (System Switch)
a639 | becf5e9e-cf74-4b70-b278-21cdaa2c0057 | BV_STA_ADZM_AMEV1 |  |  | X | X |  | X | X | 1.2.2; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} |  | Hand-Off | Speed Specification | >0* | [5 empty] | 500 | active |  | {t,t,t} | Alarm | * | * | *** | {t} |  |  |  |  | >8
a640 | 5b4952dc-be53-4f95-8ece-0c33b35003db | BV_STA_P2M_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} |  | Pump 1 | Pump 2 |  | >0* | [12 empty] | {t} |  |  |  |  | >8
a641 | 6233a058-1046-482e-88ea-5bad4a123bfe | BV_STA_E2M_AMEV1 |  |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} |  | Producer 1 | Producer 2 |  | >0* | [12 empty] | {t} |  |  |  |  | >8
a642 | 188b0278-4ad5-4b3c-99e0-59a09992936c | BV_STA_E_AMEV1 | Lighting |  | X |  |  | X | X | 1.2.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} |  | Off | On | [14 empty] | {f} |  |  |  |  | >8
|  | * B (Builder/Operator), P (Planning), X (Executing Company) | [8 empty] | Default value (parameterization) and test value | [9 empty] | [] => Default value (suggestion) | [11 empty] | * Can be used for testing in the 1:1 test
[11 empty] | Test value (internally generated value) | [9 empty] | 1 Only when execution control is performed via intrinsic alarming | [11 empty] | ** Suppress alarms when the system is switched off
*** Implementation in accordance with Chapter 4.4

## 8.5 CAL
ObjSort + LfdNr | UUID | Objekt-Template- Kennung | Kommentar | GA-FL Einträge (1.3.2) | GA-FL Einträge (3.1.1) | GA-FL Einträge (3.1.3) | GA-FL Einträge (Abschnitte/Spalten) | Object_Name | Description | Verwendung | Date_List | Letztmalige Änderung in Version
|  | PropSort | [5 empty] | a11 | a12 |  | e11
|  | Conformance Code | [5 empty] | RC | W |  | W
|  | Grundlegende Vorgabe * | [5 empty] | B * | B |  | B
|  | Detailierte Festlegung * | [5 empty] | P * | P |  | P
|  | Umsetzung * | [5 empty] | U * | U |  | U
|  | Vorgabewert (Parametrierung) | [5 empty] | ja | ja | nein | ja
d101 | ff46b697-9506-499b-accc-c82559405c4d | CAL_FT_AMEV1 |  | X | X | X | 1.3.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Jahreskalender Feiertage | [Eintrag von MBE oder lokal muss in DateList erscheinen]
d102 | cd821b14-26b0-4f4f-b109-d70e012c649d | CAL_SF_AMEV1 |  | X | X | X | 1.3.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Jahreskalender Schulferien | [Eintrag von MBE oder lokal muss in DateList erscheinen]
d103 | a3a3302a-bc55-4d5e-a56e-92c667af0015 | CAL_BF_AMEV1 |  | X | X | X | 1.3.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Jahreskalender Betriebsferien | [Eintrag von MBE oder lokal muss in DateList erscheinen]
d104 | 2b726f84-66fb-4229-a8e2-7a30cab3fdbc | CAL_ALG_AMEV1 |  | X | X | X | 1.3.2; 3.1.1; 3.1.3 | [BAS] | [Description] | Jahreskalender [frei wählbar] | [Eintrag von MBE oder lokal muss in DateList erscheinen]
|  | * B (Bauherr/Betreiber), P (GA-Planung), U (Ausführendes Unternehmen) | [5 empty] | Vorgabewert (Parametrierung) und Prüfwert
ENGLISH VERSION (Draft)
ObjSort + No. | UUID | Object Template Identifier | Comment | BACS FL entries (1.3.2) | BACS FL entries (3.1.1) | BACS FL entries (3.1.3) | BACS FL entries (sections/columns) | Object_Name | Description | Application | Date_List | Last change in version
|  | PropSort | [5 empty] | a11 | a12 |  | e11
|  | Conformance Code | [5 empty] | RC | W |  | W
|  | Basic spezification * | [5 empty] | B * | B |  | B
|  | Detailed definition * | [5 empty] | P * | P |  | P
|  | Implementation * | [5 empty] | X * | X |  | X
|  | Default value (parameterization) | [5 empty] | yes | yes | no | yes
d101 | ff46b697-9506-499b-accc-c82559405c4d | CAL_FT_AMEV1 |  | X | X | X | 1.3.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Annual calendar holidays | [Entry from MOU or locally must appear in DateList]
d102 | cd821b14-26b0-4f4f-b109-d70e012c649d | CAL_SF_AMEV1 |  | X | X | X | 1.3.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Annual calendar school holidays | [Entry from MOU or locally must appear in DateList]
d103 | a3a3302a-bc55-4d5e-a56e-92c667af0015 | CAL_BF_AMEV1 |  | X | X | X | 1.3.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Annual calendar company holidays | [Entry from MOU or locally must appear in DateList]
d104 | 2b726f84-66fb-4229-a8e2-7a30cab3fdbc | CAL_ALG_AMEV1 |  | X | X | X | 1.3.2; 3.1.1; 3.1.3 | [UAK] | [Description] | Annual calendar [freely selectable] | [Entry from MOU or locally must appear in DateList]
|  | * B (Builder/Operator), P (Planning), X (Executing Company) | [5 empty] | Default value (parameterization) and test value

## 8.6 DEV
ObjSort + LfdNr | UUID | Objekt-Template- Kennung | Kommentar | GA-FL Einträge (1.3.5) | GA-FL Einträge (3.1.1) | GA-FL Einträge (3.1.3) | GA-FL Einträge (Bemerkung, 4) | GA-FL Einträge (Abschnitte/Spalten) | Object_Name | Description | Location | Protocol_Version | Protocol_Revision | Protocol_Services_Supported | Protocol_Object_Types_Supported | Local_Time | Local_Date | UTC_Offset | Time_Synchronization_Recipients | Max_Master | Max_Info_Frames | UTC_Time_Synchronization_Recipients | Time_Synchronization_Interval | Align_Intervals | Interval_Offset | Letztmalige Änderung in Version
|  | PropSort | [6 empty] | a11 | a12 | y11 | y12 | y13 | y14 | y15 |  |  | y16 | y18 | y22 | y23 | y17 | y19 | y20 | y21
|  | Conformance Code | [6 empty] | R | W | W | R | R | R | R | R | R | W | W | W | W | W | W | R | R
|  | Grundlegende Vorgabe * | [6 empty] | B * | B | B | B | B | B | B |  |  | B | B | B | B | B | B | B | B
|  | Detailierte Festlegung * | [6 empty] | P * | P | P | P | P | P | P |  |  | P | P | P | P | P | P | P | P
|  | Umsetzung * | [6 empty] | U * | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U
|  | Vorgabewert (Parametrierung) | [6 empty] | ja | ja | ja | ja | ja | ja | ja | nein | nein | ja | ja | ja bei MS/TP | ja bei MS/TP | ja | ja | ja | ja
y101 | 51476bb9-5db6-495d-87ae-363895557c18 | DEV_AMEV1 |  | X | X | X | DEV | 1.3.5 + [Bemerkung] DEV; 3.1.1; 3.1.3 | [BAS] | [gemäß Vorgaben] | [gemäß Vorgaben] | 1 | >=14 | device, analog-input, analog-output, analog-value, binary-input, binary-output, binary-value, multi-state-value, notification-class, event-enrollment, trend-log, calendar, schedule, loop, file, [weitere erlaubt] | i-Am, who-Is, who-Has, i-Have, readProperty, readPropertyMultiple, readRange, writeProperty, writePropertyMultiple, createObject, deleteObject, confirmedEventNotification, unconfirmedEventNotification, acknowledgeAlarm, getEventInformation, timeSynchronization, utcTimeSynchronization, subscribeCOV, subscribeCOVProperty, confirmedCOVNotification, unconfirmedCOVNotification, deviceCommunicationControl, reinitializeDevice, atomicReadFile |  |  | -60 | Gemäß Zeitsynchronisationskonzept | [korrekt einstellen, nicht 127 bei MSTP-Controllern!]**** | [gemäß Vorgaben]**** | Gemäß Zeitsynchronisationskonzept | Gemäß Zeitsynchronisationskonzept | Gemäß Zeitsynchronisationskonzept | Gemäß Zeitsynchronisationskonzept | AMEV1.1
|  | * B (Bauherr/Betreiber), P (GA-Planung), U (Ausführendes Unternehmen) | [6 empty] | Vorgabewert (Parametrierung) und Prüfwert | [6 empty] | **** entfällt bei Unterstützung von Network Port Objekt
ENGLISH VERSION (Draft)
ObjSort + No. | UUID | Object Template Identifier | Comment | BACS FL entries (1.3.5) | BACS FL entries (3.1.1) | BACS FL entries (3.1.3) | BACS FL entries (Remarks, 4) | BACS FL entries (sections/columns) | Object_Name | Description | Location | Protocol_Version | Protocol_Revision | Protocol_Services_Supported | Protocol_Object_Types_Supported | Local_Time | Local_Date | UTC_Offset | Time_Synchronization_Recipients | Max_Master | Max_Info_Frames | UTC_Time_Synchronization_Recipients | Time_Synchronization_Interval | Align_Intervals | Interval_Offset | Last change in version
|  | PropSort | [6 empty] | a11 | a12 | y11 | y12 | y13 | y14 | y15 |  |  | y16 | y18 | y22 | y23 | y17 | y19 | y20 | y21
|  | Conformance Code | [6 empty] | R | W | W | R | R | R | R | R | R | W | W | W | W | W | W | R | R
|  | Basic spezification * | [6 empty] | B * | B | B | B | B | B | B |  |  | B | B | B | B | B | B | B | B
|  | Detailed definition * | [6 empty] | P * | P | P | P | P | P | P |  |  | P | P | P | P | P | P | P | P
|  | Implementation * | [6 empty] | X * | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X
|  | Default value (parameterization) | [6 empty] | yes | yes | yes | yes | yes | yes | yes | no | no | yes | yes | yes at MS/TP | yes at MS/TP | yes | yes | yes | yes
y101 | 51476bb9-5db6-495d-87ae-363895557c18 | DEV_AMEV1 |  | X | X | X | DEV | 1.3.5 + [Remarks] DEV; 3.1.1; 3.1.3 | [UAK] | [according to specifications] | [according to specifications] | 1 | >=14 | device, analog-input, analog-output, analog-value, binary-input, binary-output, binary-value, multi-state-value, notification-class, event-enrollment, trend-log, calendar, schedule, loop, file, [weitere erlaubt] | i-Am, who-Is, who-Has, i-Have, readProperty, readPropertyMultiple, readRange, writeProperty, writePropertyMultiple, createObject, deleteObject, confirmedEventNotification, unconfirmedEventNotification, acknowledgeAlarm, getEventInformation, timeSynchronization, utcTimeSynchronization, subscribeCOV, subscribeCOVProperty, confirmedCOVNotification, unconfirmedCOVNotification, deviceCommunicationControl, reinitializeDevice, atomicReadFile |  |  | -60 | According to the time synchronization concept | [set correctly, not 127 for MSTP controllers!]**** | [according to specifications]**** | According to the time synchronization concept | According to the time synchronization concept | According to the time synchronization concept | According to the time synchronization concept | AMEV1.1
|  | * B (Builder/Operator), P (Planning), X (Executing Company) | [6 empty] | Default value (parameterization) and test value | [6 empty] | **** not applicable if network port object is supported

## 8.7 EE
ObjSort + LfdNr | UUID | Objekt-Template- Kennung | Kommentar | GA-FL Einträge (1.3.5) | GA-FL Einträge (2.2.1) | GA-FL Einträge (2.2.4) | GA-FL Einträge (3.1.1) | GA-FL Einträge (3.1.3) | GA-FL Einträge (Bemerkung, 4) | GA-FL Einträge (Abschnitte/Spalten) | Object_Name | Description | Verwendung | Event_Type | Notify_Type | Event_Parameters | Object_Property_Reference | Event_State | Event_Enable | Notification_Class | Event_Time_Stamps | Event_Message_Texts | Event_Message_Texts_Config | Event_Detection_Enable | Event_Algorithm_Inhibit(_Ref) | Time_Delay_Normal | Status_Flags | Reliability | Reliability_Evaluation_Inhibit | Letztmalige Änderung in Version
|  | PropSort | [8 empty] | a11 | a12 |  | c23 | c13 | c24 | c51 |  | c12 | c11 |  |  | c14 | c15 | c41¦c42 | c44
|  | Conformance Code | [8 empty] | RC | W |  | W | W | W | W | R | W | W | R | R | W | W | RA | W | R | W1 | RX¦O
|  | Grundlegende Vorgabe * | [8 empty] | B * | B |  | B | B | B | P |  | B | B |  |  | B | B | P | P
|  | Detailierte Festlegung * | [8 empty] | P * | P |  | P | P | P | P |  | P | P |  |  | P | P | P | P
|  | Umsetzung * | [8 empty] | U * | U |  | U | U | U | U | U | U | U |  |  | U | U | U | U | U | U | U
|  | Vorgabewert (Parametrierung) | [8 empty] | ja | ja |  | ja | ja | ja | nein | nein | ja | ja | nein | nein | ja | ja | nein | ja | nein | nein | nein
b201 | 274fccea-57de-4f64-9b86-ead4409356a7 | EE_CCP_AMEV1 |  | X | X |  | X | X | EE-CCP | 1.3.5 + [Bemerkung] EE-CCP; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Handmeldung | Current_Command_Priority | Alarm | time-delay=1¦ Überprüfen |  | 0 | {t,t,t} | 500 | * | * | *** | {t} |  | 1 | {f,f,f,f} | 0
b202 | 608dca13-ae00-4329-a3dc-a7bb8ca99f02 | EE_COS_AMEV1 |  | X | X |  | X | X | EE-COS | 1.3.5 + [Bemerkung] EE-COS; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Meldung | Change_of_State | Alarm | time-delay=1¦BACnetPropertyStates=[active] |  | 0 | {t,t,t} | [**] | * | * | *** | {t} |  | 1 | {f,f,f,f} | 0
b203 | 22e1dfce-b10e-4f67-a1e1-cb5d219d0a91 | EE_OOR_AMEV1 |  | X | X |  | X | X | EE-OOR | 1.3.5 + [Bemerkung] EE-OOR; 2.2.1;3.1.1; 3.1.3 | [BAS] | [Description] | Meldung | Out_Of_Range | Alarm | time-delay=[**]¦low-limit=[**]¦high-limit=[**]¦deadband=[**] |  | 0 | {t,t,t} | [**] | * | * | *** | {t} |  | 1 | {f,f,f,f} | 0
b204 | 5740e127-4268-4cf9-8b1f-040fa417bde8 | EE_FLIM_AMEV1 |  | X |  | X | X | X | EE-FLIM | 1.3.5 + [Bemerkung] EE-FLIM; 2.2.4; 3.1.1; 3.1.3 | [BAS] | [Description] | Abweichung | Floating_Limit | Alarm | time-delay=[**]¦setpoint-reference=[**]¦low-diff-limit=[**]¦high-diff-limit=[**]¦deadband=[**] |  | 0 | {t,t,t} | [300] | * | * | *** | {t} |  | 1 | {f,f,f,f} | 0
b205 | 3fa5e4cb-75a3-4194-8e50-1fa8ec768dbb | EE_COB_AMEV1 |  | X | X |  | X | X | EE-COB | 1.3.5 + [Bemerkung] EE-CCP; 2.2.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Handmeldung | Change_of_Bitstring | Alarm | time-delay=1¦bitmask=[out-of-service¦overridden]¦list-of-bitstring-values=[f,f,t,t] |  | 0 | {t,t,t} | 500 | * | * | *** | {t} |  | 1 | {f,f,f,f} | 0 |  | AMEV1.1
b206 | e4fba20a-bcd4-4395-a310-13319904ba5d | EE_COV_AMEV1 |  | X |  |  | X | X | EE-COV | 1.3.5 + [Bemerkung] EE-COV; 3.1.1; 3.1.3 | [BAS] | [Description] | Wertänderung | Change_Of_Value | Alarm | time-delay=0¦cov-criteria=[**] |  | 0 | {t,t,t} | [**] | * | * | *** | {t} |  | 1 | {f,f,f,f} | 0
b207 | fbd7ed6d-5040-4a91-b13c-6f517b049f5f | EE_GM_PSA_AMEV1 |  | X |  | X | X | X | EE-CMDF | 1.3.5 + [Bemerkung] EE-FLIM; 2.2.4; 3.1.1; 3.1.3 | [BAS] | [Description] | Gefahrmeldung Personenschutz | Command Failure | Alarm | time-delay=[**]¦feedback-property-reference=[**] |  | 0 | {t,t,t} | [100] | * | * | *** | {t} |  | 1 | {f,f,f,f} | 0 |  | AMEV1.1
b208 | 1dffa477-971c-4908-b5c8-a75feb76e5b6 | EE_CMDF_AMEV1 |  | X |  | X | X | X | EE-CMDF | 1.3.5 + [Bemerkung] EE-FLIM; 2.2.4; 3.1.1; 3.1.3 | [BAS] | [Description] | Ausführkontrolle | Command Failure | Alarm | time-delay=[**]¦feedback-property-reference=[**] |  | 0 | {t,t,t} | [300] | * | * | *** | {t} |  | 1 | {f,f,f,f} | 0 |  | AMEV1.1
|  | * B (Bauherr/Betreiber), P (GA-Planung), U (Ausführendes Unternehmen) | [8 empty] | Vorgabewert (Parametrierung) und Prüfwert | [9 empty] | * Kann zur Prüfung beim 1:1 Test herangezogen werden
[11 empty] | Prüfwert (systemintern erzeugter Wert) | [11 empty] | *** gemäß Kapitel 4.4 einrichten
ENGLISH VERSION (Draft)
ObjSort + No. | UUID | Object Template Identifier | Comment | BACS FL entries (1.3.5) | BACS FL entries (2.2.1) | BACS FL entries (2.2.4) | BACS FL entries (3.1.1) | BACS FL entries (3.1.3) | BACS FL entries (Remarks, 4) | BACS FL entries (sections/columns) | Object_Name | Description | Application | Event_Type | Notify_Type | Event_Parameters | Object_Property_Reference | Event_State | Event_Enable | Notification_Class | Event_Time_Stamps | Event_Message_Texts | Event_Message_Texts_Config | Event_Detection_Enable | Event_Algorithm_Inhibit(_Ref) | Time_Delay_Normal | Status_Flags | Reliability | Reliability_Evaluation_Inhibit | Last change in version
|  | PropSort | [8 empty] | a11 | a12 |  | c23 | c13 | c24 | c51 |  | c12 | c11 |  |  | c14 | c15 | c41¦c42 | c44
|  | Conformance Code | [8 empty] | RC | W |  | W | W | W | W | R | W | W | R | R | W | W | RA | W | R | W1 | RX¦O
|  | Basic spezification * | [8 empty] | B * | B |  | B | B | B | P |  | B | B |  |  | B | B | P | P
|  | Detailed definition * | [8 empty] | P * | P |  | P | P | P | P |  | P | P |  |  | P | P | P | P
|  | Implementation * | [8 empty] | X * | X |  | X | X | X | X | X | X | X |  |  | X | X | X | X | X | X | X
|  | Default value (parameterization) | [8 empty] | yes | yes |  | yes | yes | yes | no | no | yes | yes | no | no | yes | yes | no | yes | no | no | no
b201 | 274fccea-57de-4f64-9b86-ead4409356a7 | EE_CCP_AMEV1 |  | X | X |  | X | X | EE-CCP | 1.3.5 + [Remarks] EE-CCP; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Local override message | Current_Command_Priority | Alarm | time-delay=1¦ Überprüfen |  | 0 | {t,t,t} | 500 | * | * | *** | {t} |  | 1 | {f,f,f,f} | 0
b202 | 608dca13-ae00-4329-a3dc-a7bb8ca99f02 | EE_COS_AMEV1 |  | X | X |  | X | X | EE-COS | 1.3.5 + [Remarks] EE-COS; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Message | Change_of_State | Alarm | time-delay=1¦BACnetPropertyStates=[active] |  | 0 | {t,t,t} | [**] | * | * | *** | {t} |  | 1 | {f,f,f,f} | 0
b203 | 22e1dfce-b10e-4f67-a1e1-cb5d219d0a91 | EE_OOR_AMEV1 |  | X | X |  | X | X | EE-OOR | 1.3.5 + [Remarks] EE-OOR; 2.2.1;3.1.1; 3.1.3 | [UAK] | [Description] | Message | Out_Of_Range | Alarm | time-delay=[**]¦low-limit=[**]¦high-limit=[**]¦deadband=[**] |  | 0 | {t,t,t} | [**] | * | * | *** | {t} |  | 1 | {f,f,f,f} | 0
b204 | 5740e127-4268-4cf9-8b1f-040fa417bde8 | EE_FLIM_AMEV1 |  | X |  | X | X | X | EE-FLIM | 1.3.5 + [Remarks] EE-FLIM; 2.2.4; 3.1.1; 3.1.3 | [UAK] | [Description] | Deviation | Floating_Limit | Alarm | time-delay=[**]¦setpoint-reference=[**]¦low-diff-limit=[**]¦high-diff-limit=[**]¦deadband=[**] |  | 0 | {t,t,t} | [300] | * | * | *** | {t} |  | 1 | {f,f,f,f} | 0
b205 | 3fa5e4cb-75a3-4194-8e50-1fa8ec768dbb | EE_COB_AMEV1 |  | X | X |  | X | X | EE-COB | 1.3.5 + [Remarks] EE-CCP; 2.2.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Local override message | Change_of_Bitstring | Alarm | time-delay=1¦bitmask=[out-of-service¦overridden]¦list-of-bitstring-values=[f,f,t,t] |  | 0 | {t,t,t} | 500 | * | * | *** | {t} |  | 1 | {f,f,f,f} | 0 |  | AMEV1.1
b206 | e4fba20a-bcd4-4395-a310-13319904ba5d | EE_COV_AMEV1 |  | X |  |  | X | X | EE-COV | 1.3.5 + [Remarks] EE-COV; 3.1.1; 3.1.3 | [UAK] | [Description] | Change in value | Change_Of_Value | Alarm | time-delay=0¦cov-criteria=[**] |  | 0 | {t,t,t} | [**] | * | * | *** | {t} |  | 1 | {f,f,f,f} | 0
b207 | fbd7ed6d-5040-4a91-b13c-6f517b049f5f | EE_GM_PSA_AMEV1 |  | X |  | X | X | X | EE-CMDF | 1.3.5 + [Remarks] EE-FLIM; 2.2.4; 3.1.1; 3.1.3 | [UAK] | [Description] | Hazard alarm personal protection | Command Failure | Alarm | time-delay=[**]¦feedback-property-reference=[**] |  | 0 | {t,t,t} | [100] | * | * | *** | {t} |  | 1 | {f,f,f,f} | 0 |  | AMEV1.1
b208 | 1dffa477-971c-4908-b5c8-a75feb76e5b6 | EE_CMDF_AMEV1 |  | X |  | X | X | X | EE-CMDF | 1.3.5 + [Remarks] EE-FLIM; 2.2.4; 3.1.1; 3.1.3 | [UAK] | [Description] | Execution control | Command Failure | Alarm | time-delay=[**]¦feedback-property-reference=[**] |  | 0 | {t,t,t} | [300] | * | * | *** | {t} |  | 1 | {f,f,f,f} | 0 |  | AMEV1.1
|  | * B (Builder/Operator), P (Planning), X (Executing Company) | [8 empty] | Default value (parameterization) and test value | [9 empty] | * Can be used for testing in the 1:1 test
[11 empty] | Test value (internally generated value) | [11 empty] | *** Implementation according to Chapter 4.4

## 8.8 LP
ObjSort + LfdNr | UUID | Objekt-Template- Kennung | Kommentar | GA-FL Einträge (1.3.5) | GA-FL Einträge (3.1.1) | GA-FL Einträge (Bemerkung,4) | GA-FL Einträge (Abschnitte/Spalten) | Object_Name | Description | Verwendung | Status_Flags | Event_State | Reliability | Out_Of_Service | Output_Units | Manipulated_Variable_Reference | Controlled_Variable_Reference | Controlled_Variable_Units | Setpoint_Reference | Action | Proportional_Constant | Proportional_Constant_Units | Integral_Constant | Integral_Constant_Units | Derivative_Constant | Derivative_Constant_Units | Maximum_Output | Minimum_Output | Priority_For_Writing | COV_Increment | Time_Delay | Notification_Class | Event_Enable | Time_Delay_Normal | Error_Limit | Deadband | Low_Diff_Limit | Notify_Type | Event_Time_Stamps | Event_Message_Texts | Event_Message_Texts_Config | Event_Detection_Enable | Event_Algorithm_Inhibit(_Ref) | Reliability_Evaluation_Inhibit | Letztmalige Änderung in Version
|  | PropSort | [5 empty] | a11 | a12 | [5 empty] | f47 | f46 | f42 | f43 | f11 | f41 | f71 | f72 | f75 | f76 | f73 | f74 | f45 | f44 | b18 | b17 | c43 | c11 | c12 | c44 | f42 | c50 |  | c13 |  |  | c14 | c15 | c41¦c42
|  | Conformance Code | [5 empty] | R | W |  | R | R | R | W | R | R | R | R | R | W | W | R | W | R | W | R | W | W | R | W | W | W | W | W | W | W | W | W | R | R | W | W | RA | RX¦O
|  | Grundlegende Vorgabe * | [5 empty] | B * | B | [5 empty] | P | P | P | P | B | P | U | U | U | U | U | U | P | P | B | B | U | U | U | U | U | U | U | U | U | U | U | U | U | U
|  | Detailierte Festlegung * | [5 empty] | P * | P | bar: R to RX¦O
|  | Umsetzung * | [5 empty] | U * | U | bar: R to RX¦O
|  | Vorgabewert (Parametrierung) | [5 empty] | ja | ja | nein | nein | nein | nein | nein | nein | nein | nein | nein | ja | ja | nein | nein | nein | nein | nein | nein | ja | ja | ja | ja | ja | ja | ja | ja | ja | ja | ja | ja | nein | nein | ja | ja | nein | nein
e101 | 57a42cd9-46a9-4981-abbe-2e6a9df38efe | LP_AN_AMEV1 |  | X | X | LP | 1.3.5 + [Bemerkung] LP; 3.1.1; 3.1.3 | [BAS] | [Description] | Regler | R: {f,f,f,f}; R: 0; R: 0; W: {f}; W: [100]; W: [0]; R: 15; W: [2,5]; W: ****; W: ****; W: ****; W: ****; W: ****; W: ****; W: ****; W: ****; W: ***; W: [{f}]
|  | * B (Bauherr/Betreiber), P (GA-Planung), U (Ausführendes Unternehmen) | [5 empty] | Vorgabewert (Parametrierung) und Prüfwert |  |  | W: *** gemäß Kapitel 4.4 einrichten
[8 empty] | Prüfwert (systemintern erzeugter Wert) |  |  | W: **** Blau markierte Properties sind für AS-C u. AS-D nicht vorgeschrieben (im Gegensatz zu AS-B) .
Bei Intrinsic Reporting in Loop-Objekten werden die Properties nach den obigen Vorgaben
eingerichtet. Bitte Hinweise in BACtwin-Beschreibung Abschnitt 4.7 Loop-Objekte beachten.
ENGLISH VERSION (Draft)
ObjSort + No. | UUID | Object Template Identifier | Comment | BACS FL entries (1.3.5) | BACS FL entries (3.1.1) | BACS FL entries (Remarks, 4) | BACS FL entries (sections/columns) | Object_Name | Description | Application | Status_Flags | Event_State | Reliability | Out_Of_Service | Output_Units | Manipulated_Variable_Reference | Controlled_Variable_Reference | Controlled_Variable_Units | Setpoint_Reference | Action | Proportional_Constant | Proportional_Constant_Units | Integral_Constant | Integral_Constant_Units | Derivative_Constant | Derivative_Constant_Units | Maximum_Output | Minimum_Output | Priority_For_Writing | COV_Increment | Time_Delay | Notification_Class | Notification_Class | Time_Delay_Normal | Error_Limit | Deadband | Low_Diff_Limit | Notify_Type | Event_Time_Stamps | Event_Message_Texts | Event_Message_Texts_Config | Event_Detection_Enable | Event_Algorithm_Inhibit(_Ref) | Reliability_Evaluation_Inhibit | Last change in version
|  | PropSort | [5 empty] | a11 | a12 | [5 empty] | f47 | f46 | f42 | f43 | f11 | f41 | f71 | f72 | f75 | f76 | f73 | f74 | f45 | f44 | b18 | b17 | c43 | c11 | c11 | c44 | f42 | c50 |  | c13 |  |  | c14 | c15 | c41¦c42
|  | Conformance Code | [5 empty] | R | W |  | R | R | R | W | R | R | R | R | R | W | W | R | W | R | W | R | W | W | R | W | W | W | W | W | W | W | W | W | R | R | W | W | RA | RX¦O
|  | Basic spezification * | [5 empty] | B * | B | [5 empty] | P | P | P | P | B | P | X | X | X | X | X | X | P | P | B | B | X | X | X | X | X | X | X | X | X | X | X | X | X | X
|  | Detailed definition * | [5 empty] | P * | P | bar: R to RX¦O
|  | Implementation * | [5 empty] | X * | X | bar: R to RX¦O
|  | Default value (parameterization) | [5 empty] | yes | yes | no | no | no | no | no | no | no | no | no | yes | yes | no | no | no | no | no | no | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | no | no | yes | yes | no | no
e101 | 57a42cd9-46a9-4981-abbe-2e6a9df38efe | LP_AN_AMEV1 |  | X | X | LP | 1.3.5 + [Remarks] LP; 3.1.1; 3.1.3 | [UAK] | [Description] | Loop | R: {f,f,f,f}; R: 0; R: 0; W: {f}; W: [100]; W: [0]; R: 15; W: [2,5]; W: ****; W: ****; W: ****; W: ****; W: ****; W: ****; W: ****; W: ****; W: ***; W: [{f}]
|  | * B (Builder/Operator), P (Planning), X (Executing Company) | [5 empty] | Default value (parameterization) and test value |  |  | W: *** Implementation according to Chapter 4.4
[8 empty] | Test value (internally generated value) |  |  | W: **** Properties marked in blue are not required for AS-C and AS-D (unlike AS-B).
For intrinsic reporting in loop objects, the properties are set up according to the above
specifications. Please refer to the BACtwin description section 4.7 Loop Objects.

## 8.9 MI
ObjSort + LfdNr | UUID | Objekt-Template- Kennung | Kommentar | GA-FL Einträge (1.1.2) | GA-FL Einträge (2.2.1) | GA-FL Einträge (3.1.1) | GA-FL Einträge (3.1.3) | GA-FL Einträge (Abschnitte/Spalten) | Object_Name | Description | Verwendung | Status_Flags | Event_State | Reliability | Out_Of_Service | Number_Of_States | State_Text | Time_Delay | Notification_Class | Alarm_Values | Fault_Values | Event_Enable | Notify_Type | Event_Time_Stamps | Event_Message_Texts | Event_Message_Texts_Config | Event_Detection_Enable | Event_Algorithm_Inhibit(_Ref) | Time_Delay_Normal | Reliability_Evaluation_Inhibit | Letztmalige Änderung in Version
|  | PropSort | [6 empty] | a11 | a12 | [5 empty] | b42 | b15 | c43 | c11 | c17 | c18 | c12 | c13 |  |  | c14 | c15 | c41¦c42 | c44
|  | Conformance Code | [6 empty] | R | W |  | R | R | W1 | W | R | W | W | W | W | W | W | W | R | R | W | W | RA | W | RX¦O
|  | Grundlegende Vorgabe * | [6 empty] | B * | B | [6 empty] | B | P | B | B | B | B | B |  |  | B | B | P | P
|  | Detailierte Festlegung * | [6 empty] | P * | P | [6 empty] | P | P | P | P | P | P | P |  |  | P | P | P | P
|  | Umsetzung * | [6 empty] | U * | U |  | U | U | U | U | U | U | U | U | U | U | U | U |  |  | U | U | U | U | U
|  | Vorgabewert (Parametrierung) | [6 empty] | ja | ja |  | nein | nein | nein | nein | nein | ja | ja | ja | ja | ja | ja | ja | nein | nein | ja | ja | nein | ja | nein
a701 | 707841a1-beaa-4e67-8fda-11bab8a85fea | MI_HD_AEM_AMEV1 |  | 3 | 2 | X | X | 1.1.2 = 3; 2.2.1 = 2; 3.1.1; 3.1.3 | [BAS] | [Description] | Handmeldung | {f,f,f,f} | 0 | 0 | {f} | 3 | Aus, Ein, Auto | 1 | 500 | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1
a702 | d91d809c-77c2-4193-a76e-5341a5687965 | MI_HD_ASGM_AMEV1 |  | 3 | 2 | X | X | 1.1.2 = 3; 2.2.1 = 2; 3.1.1; 3.1.3 | [BAS] | [Description] | Handmeldung | {f,f,f,f} | 0 | 0 | {f} | 3 | Aus, Stellgröße, Auto | 1 | 500 | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1
a703 | f53fb3ec-1c21-46dd-99ea-fef645731eb5 | MI_HD_A2nM_AMEV1 |  | 4 | 3 | X | X | 1.1.2 = 4; 2.2.1 = 3; 3.1.1; 3.1.3 | [BAS] | [Description] | Handmeldung | {f,f,f,f} | 0 | 0 | {f} | 4 | Aus, Stufe 1, Stufe 2, Auto | 1 | 500 | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1
a709 | 8ade70cc-9bb3-4d59-af1f-55fa70010f2c | MI_HD_A2HDM_AMEV1 |  | 4 | 3 | X | X | 1.2.2 = 4; 2.2.1 = 3; 3.1.1; 3.1.3 | [BAS] | [Description] | Handmeldung | {f,f,f,f} | 0 | 0 | {f} | 4 | Aus, Zu, Auf ,Auto | 1 | 500 | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | AMEV1.1
a704 | c8d891a2-73fc-432e-9bb3-83421999bff5 | MI_HD_AnM_AMEV1 |  | 3 | 2 | X | X | 1.1.2 = 3; 2.2.1 = 2; 3.1.1; 3.1.3 | [BAS] | [Description] | Handmeldung | {f,f,f,f} | 0 | 0 | {f} | 3 | Aus, Drehzahl-Vorgabe, Auto | 1 | 500 | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1
a705 | 6fba454c-7f8a-471d-9c92-d13d517a144b | MI_RM_ZKA_AMEV1 |  | 3 | 2 | X | X | 1.1.2 = 3; 2.2.1 = 2; 3.1.1; 3.1.3 | [BAS] | [Description] | Rückmeldung | {f,f,f,f} | 0 | 0 | {f} | 3 | Zu, gekippt, Auf | [600] | 500 | <>Zu |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1
a706 | 9768d661-66bf-43c8-94fe-414781747df1 | MI_ZAF_ETS_AMEV1 |  | n |  | X | X | 1.1.2 = n; 3.1.1; 3.1.3 | [BAS] | [Description] | Etagenstand | {f,f,f,f} | 0 | 0 | {f} | n | [U2,U2,E,1,2,3…] | [6 empty] | * | * |  | {f} |  | 1
a707 | af65f65a-885c-4fba-9665-e927e2485c89 | MI_BM_2n_AMEV1 |  | 3 |  | X | X | 1.1.2 = 3; 3.1.1; 3.1.3 | [BAS] | [Description] | Betriebsmeldung 2 stufig | {f,f,f,f} | 0 | 0 | {f} | 3 | Aus, Stufe 1, Stufe 2 | [6 empty] | * | * |  | {f} |  | 1
a708 | 23c63b63-6f83-4a4d-a7e6-451030c2ee92 | MI_BM_3n_AMEV1 |  | 4 |  | X | X | 1.1.2 = 4; 3.1.1; 3.1.3 | [BAS] | [Description] | Betriebsmeldung 3 stufig | {f,f,f,f} | 0 | 0 | {f} | 4 | Aus, Stufe 1, Stufe 2, Stufe 3 | [6 empty] | * | * |  | {f} |  | 1
|  | * B (Bauherr/Betreiber), P (GA-Planung), U (Ausführendes Unternehmen) | [6 empty] | Vorgabewert (Parametrierung) und Prüfwert | [13 empty] | *Kann zur Prüfung des 1:1 Test herangezogen werden
[9 empty] | Prüfwert (systemintern erzeugter Wert) | [16 empty] | *** gemäß Kapitel 4.4 einrichten
ENGLISH VERSION (Draft)
ObjSort + No. | UUID | Object Template Identifier | Comment | BACS FL entries (1.1.2) | BACS FL entries (2.2.1) | BACS FL entries (3.1.1) | BACS FL entries (3.1.3) | BACS FL entries (sections/columns) | Object_Name | Description | Application | Status_Flags | Event_State | Reliability | Out_Of_Service | Number_Of_States | State_Text | Time_Delay | Notification_Class | Alarm_Values | Fault_Values | Event_Enable | Notify_Type | Event_Time_Stamps | Event_Message_Texts | Event_Message_Texts_Config | Event_Detection_Enable | Event_Algorithm_Inhibit(_Ref) | Time_Delay_Normal | Reliability_Evaluation_Inhibit | Last change in version
|  | PropSort | [6 empty] | a11 | a12 | [5 empty] | b42 | b15 | c43 | c11 | c17 | c18 | c12 | c13 |  |  | c14 | c15 | c41¦c42 | c44
|  | Conformance Code | [6 empty] | R | W |  | R | R | W1 | W | R | W | W | W | W | W | W | W | R | R | W | W | RA | W | RX¦O
|  | Basic spezification * | [6 empty] | B * | B | [6 empty] | B | P | B | B | B | B | B |  |  | B | B | P | P
|  | Detailed definition * | [6 empty] | P * | P | [6 empty] | P | P | P | P | P | P | P |  |  | P | P | P | P
|  | Implementation * | [6 empty] | X * | X |  | X | X | X | X | X | X | X | X | X | X | X | X |  |  | X | X | X | X | X
|  | Default value (parameterization) | [6 empty] | yes | yes |  | no | no | no | no | no | yes | yes | yes | yes | yes | yes | yes | no | no | yes | yes | no | yes | no
a701 | 707841a1-beaa-4e67-8fda-11bab8a85fea | MI_HD_AEM_AMEV1 |  | 3 | 2 | X | X | 1.1.2 = 3; 2.2.1 = 2; 3.1.1; 3.1.3 | [UAK] | [Description] | Local Override Message | {f,f,f,f} | 0 | 0 | {f} | 3 | Off, On, Auto | 1 | 500 | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1
a702 | d91d809c-77c2-4193-a76e-5341a5687965 | MI_HD_ASGM_AMEV1 |  | 3 | 2 | X | X | 1.1.2 = 3; 2.2.1 = 2; 3.1.1; 3.1.3 | [UAK] | [Description] | Local Override Message | {f,f,f,f} | 0 | 0 | {f} | 3 | Off, Control Variable, Auto | 1 | 500 | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1
a703 | f53fb3ec-1c21-46dd-99ea-fef645731eb5 | MI_HD_A2nM_AMEV1 |  | 4 | 3 | X | X | 1.1.2 = 4; 2.2.1 = 3; 3.1.1; 3.1.3 | [UAK] | [Description] | Local Override Message | {f,f,f,f} | 0 | 0 | {f} | 4 | Off, Level 1, Level 2, Auto | 1 | 500 | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1
a709 | 8ade70cc-9bb3-4d59-af1f-55fa70010f2c | MI_HD_A2HDM_AMEV1 |  | 4 | 3 | X | X | 1.2.2 = 4; 2.2.1 = 3; 3.1.1; 3.1.3 | [UAK] | [Description] | Local Override Message | {f,f,f,f} | 0 | 0 | {f} | 4 | Off, Closed, Open ,Auto | 1 | 500 | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | AMEV1.1
a704 | c8d891a2-73fc-432e-9bb3-83421999bff5 | MI_HD_AnM_AMEV1 |  | 3 | 2 | X | X | 1.1.2 = 3; 2.2.1 = 2; 3.1.1; 3.1.3 | [UAK] | [Description] | Local Override Message | {f,f,f,f} | 0 | 0 | {f} | 3 | Off, RPM Preset, Auto | 1 | 500 | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1
a705 | 6fba454c-7f8a-471d-9c92-d13d517a144b | MI_RM_ZKA_AMEV1 |  | 3 | 2 | X | X | 1.1.2 = 3; 2.2.1 = 2; 3.1.1; 3.1.3 | [UAK] | [Description] | Feedback | {f,f,f,f} | 0 | 0 | {f} | 3 | Closed, Tilted, On | [600] | 500 | <>Closed |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | AMEV1.1
a706 | 9768d661-66bf-43c8-94fe-414781747df1 | MI_ZAF_ETS_AMEV1 |  | n |  | X | X | 1.1.2 = n; 3.1.1; 3.1.3 | [UAK] | [Description] | Floor Indicator | {f,f,f,f} | 0 | 0 | {f} | n | [U2,U2,E,1,2,3...] | [6 empty] | * | * |  | {f} |  | 1
a707 | af65f65a-885c-4fba-9665-e927e2485c89 | MI_BM_2n_AMEV1 |  | 3 |  | X | X | 1.1.2 = 3; 3.1.1; 3.1.3 | [UAK] | [Description] | Operating Message Two-stage | {f,f,f,f} | 0 | 0 | {f} | 3 | Off, Level 1, Level 2 | [6 empty] | * | * |  | {f} |  | 1
a708 | 23c63b63-6f83-4a4d-a7e6-451030c2ee92 | MI_BM_3n_AMEV1 |  | 4 |  | X | X | 1.1.2 = 4; 3.1.1; 3.1.3 | [UAK] | [Description] | Operating Message Three-stage | {f,f,f,f} | 0 | 0 | {f} | 4 | Off, Level 1, Level 2, Level 3 | [6 empty] | * | * |  | {f} |  | 1
|  | * B (Builder/Operator), P (Planning), X (Executing Company) | [6 empty] | Default value (parameterization) and test value | [14 empty] | * Can be used for testing in the 1:1 test
[9 empty] | Test value (internally generated value) | [14 empty] | *** Implementation according to Chapter 4.3

## 8.10 MO_MV
ObjSort + LfdNr | UUID | Objekt-Template- Kennung | Kommentar | GA-FL Einträge (1.1.2) | GA-FL Einträge (1.2.2) | GA-FL Einträge (2.2.1) | GA-FL Einträge (2.2.4) | GA-FL Einträge (3.1.1) | GA-FL Einträge (3.1.3) | GA-FL Einträge (Abschnitte/Spalten) | Object_Name | Description | Verwendung | Status_Flags | Event_State | Reliability | Out_Of_Service | Number_Of_States | State_Text | Relinquish_Default | Time_Delay | Notification_Class | Feedback_Value (nur MO) | Alarm_Values (nur MV) | Fault_Values (nur MV) | Event_Enable | Notify_Type | Event_Time_Stamps | Event_Message_Texts | Event_Message_Texts_Config | Event_Detection_Enable | Event_Algorithm_Inhibit(_Ref) | Time_Delay_Normal | Reliability_Evaluation_Inhibit | Current_Command_Priority | Letztmalige Änderung in Version
|  | PropSort | [8 empty] | a11 | a12 | 5 |  |  |  |  | b42 | b15 | b16 | c43 | c11 | c19 | c17 | c18 | c12 | c13 |  |  | c14 | c15 | c41¦c42 | c44
|  | Conformance Code | R | [7 empty] | R | W |  | R | R | W1 | W | R | W | W | W | W | R | W | W | W | W | R | R | W | W | RA | W | RX¦O | R22
|  | Grundlegende Vorgabe * | [8 empty] | B * | B | [6 empty] | B | B | P | B | B | B | B | B | B |  |  | B | B | P | P
|  | Detailierte Festlegung * | [8 empty] | P * | P | [6 empty] | P | P | P | P | P | P | P | P | P |  |  | P | P | P | P
|  | Umsetzung * | [8 empty] | U * | U |  | U | U | U | U | U | U | U | U | U | U | U | U | U | U |  |  | U | U | U | U | U | U
|  | Vorgabewert (Parametrierung) | [8 empty] | ja | ja |  | nein | nein | nein | nein | nein | ja | ja | ja | ja | nein | ja | ja | ja | ja | nein | nein | ja | ja | nein | ja | nein | nein
Schaltbefehl
a801 | 1eece5c2-0478-4a7d-a388-a2906022ddb9 | MO_SB_ASn_AMEV1 | Stufe n | 2+n |  |  | 2+n | X | X | 1.1.2 = 2+n; 2.2.4 = 2+n; 3.1.1; 3.1.3 | [BAS] | [Description] | Schaltbefehl Anlagenschalter Stufe n | {f,f,f,f} | 0 | 0 | {f} | [2+n] | [Aus, Stufe 1, Stufe n] | Aus | [**] |  |  |  |  | {t,t,t}¹ | Alarm¹ | *¹ | *¹ | ***¹ | {t/f}¹ |  | 1¹ |  | >8
a802 | 6febdcfb-47aa-40fa-95e9-4edc49672d85 | MO_SB_2n_AMEV1 |  | 3 |  |  | 3 | X | X | 1.1.2 = 3; 2.2.4 = 3; 3.1.1; 3.1.3 | [BAS] | [Description] | Schaltbefehl 2 Stufig | {f,f,f,f} | 0 | 0 | {f} | 3 | Aus, Stufe 1, Stufe 2 | Aus | [60]¹ | 300¹ |  |  |  | {t,t,t}¹ | Alarm¹ | *¹ | *¹ | ***¹ | {t/f}¹ |  | 1¹ |  | >8
a803 | c7f5731d-e7d8-4ac9-b963-002edbe23ee5 | MO_SB_3n_AMEV1 |  | 4 |  |  | 4 | X | X | 1.1.2 = 4; 2.2.4 = 4; 3.1.1; 3.1.3 | [BAS] | [Description] | Schaltbefehl 3 Stufig | {f,f,f,f} | 0 | 0 | {f} | 4 | Aus, Stufe 1, Stufe 2, Stufe 3 | Aus | [60]¹ | 300¹ |  |  |  | {t,t,t}¹ | Alarm¹ | *¹ | *¹ | ***¹ | {t/f}¹ |  | 1¹ |  | >8
Anlagenschalter
a901 | 267ded4b-eaf4-4ee5-8b89-f14f99851646 | MV_AS_M_AMEV1 |  |  | 3 | 2 |  | X | X | 1.2.2 = 3; 2.2.1 = 2; 3.1.1; 3.1.3 | [BAS] | [Description] | Anlagensteuerung | {f,f,f,f} | 0 | 0 | {f} | 3 | [nach Vorgabe] | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a902 | 3f3ca156-5543-49fb-b8d8-774bdc96c929 | MV_GS_AEM_AMEV1 |  |  | 3 | 2 |  | X | X | 1.2.2 = 3; 2.2.1 = 2; 3.1.1; 3.1.3 | [BAS] | [Description] | Gesamtanlagensteuerung | {f,f,f,f} | 0 | 0 | {f} | 3 | Aus, Ein, Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a903 | c2854dd0-f2a9-447d-972c-88877bce48b8 | MV_AS_AEM_AMEV1 |  |  | 3 | 2 |  | X | X | 1.2.2 = 3; 2.2.1 = 2; 3.1.1; 3.1.3 | [BAS] | [Description] | Anlagensteuerung | {f,f,f,f} | 0 | 0 | {f} | 3 | Aus, Ein, Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a904 | 158e4a23-6201-4554-b8ff-3e4e3a79acfc | MV_GS_A2nM_AMEV1 |  |  | 4 | 3 |  | X | X | 1.2.2 = 4; 2.2.1 = 3; 3.1.1; 3.1.3 | [BAS] | [Description] | Gesamtanlagensteuerung | {f,f,f,f} | 0 | 0 | {f} | 4 | Aus, Stufe 1, Stufe 2, Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a905 | 59554960-0c8c-4a99-a45b-8dcc0941b141 | MV_AS_A2nM_AMEV1 |  |  | 4 | 3 |  | X | X | 1.2.2 = 4; 2.2.1 = 3; 3.1.1; 3.1.3 | [BAS] | [Description] | Anlagensteuerung | {f,f,f,f} | 0 | 0 | {f} | 4 | Aus, Stufe 1, Stufe 2, Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a906 | b52201b7-ae17-4ff8-af56-6d98ec30af64 | MV_AS_ADZM_AMEV1 |  |  | 3 | 2 |  | X | X | 1.2.2 = 3; 2.2.1 = 2; 3.1.1; 3.1.3 | [BAS] | [Description] | Anlagensteuerung | {f,f,f,f} | 0 | 0 | {f} | 3 | Aus, Drehzahlvorgabe, Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a907 | 4eeb4604-22ac-4130-ac17-be26f2a5d822 | MV_AS_AEBM_AMEV1 |  |  | 4 | 3 |  | X | X | 1.2.2 = 4; 2.2.1 = 3; 3.1.1; 3.1.3 | [BAS] | [Description] | Anlagensteuerung | {f,f,f,f} | 0 | 0 | {f} | 4 | Aus, Ein, Ein Bypass, Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a908 | 32532ddb-c336-4576-a381-c599fea37555 | MV_AS_ASWM_AMEV1 |  |  | 4 | 3 |  | X | X | 1.2.2 = 4; 2.2.1 = 3; 3.1.1; 3.1.3 | [BAS] | [Description] | Anlagensteuerung | {f,f,f,f} | 0 | 0 | {f} | 4 | Aus, Sommer, Winter, Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a909 | db6d18e4-5ff4-43d9-b7f0-297e7a722fbd | MV_AS_ASNF_AMEV1 |  |  | 4 |  |  | X | X | 1.2.2 = 4; 3.1.1; 3.1.3 | [BAS] | [Description] | Anlagensteuerung | {f,f,f,f} | 0 | 0 | {f} | 4 | Aus, Schleichfahrt, Normalfahrt, Auto | Aus | [10 empty] | {f} |  | 1 |  | >8
a910 | 1bce8316-e0ba-4413-b5ee-5728f159036d | MV_AS_A2n_AMEV1 |  |  | 3 |  |  | X | X | 1.2.2 = 3; 3.1.1; 3.1.3 | [BAS] | [Description] | Anlagensteuerung | {f,f,f,f} | 0 | 0 | {f} | 3 | Aus, Stufe 1, Stufe 2 | Aus | [10 empty] | {f} |  | 1 |  | >8
a911 | ab87b375-9283-4401-a29d-de78b7e07607 | MV_AS_A3n_AMEV1 |  |  | 4 |  |  | X | X | 1.2.2 = 4; 3.1.1; 3.1.3 | [BAS] | [Description] | Anlagensteuerung | {f,f,f,f} | 0 | 0 | {f} | 4 | Aus, Stufe 1, Stufe 2, Stufe 3 | Aus | [10 empty] | {f} |  | 1 |  | >8
a912 | 479eabb3-19a6-49a3-8bbc-c12c4538673c | MV_AS_P2M_AMEV1 |  |  | 3 | 2 |  | X | X | 1.2.2 = 3; 2.2.1 = 2; 3.1.1; 3.1.3 | [BAS] | [Description] | Anlagensteuerung | {f,f,f,f} | 0 | 0 | {f} | 3 | Pumpe 1, Pumpe 2, Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a913 | aea173d8-8859-4ea0-a14c-75cb2c40bd23 | MV_AS_P3M_AMEV1 |  |  | 4 | 3 |  | X | X | 1.2.2 = 4; 2.2.1 = 3; 3.1.1; 3.1.3 | [BAS] | [Description] | Anlagensteuerung | {f,f,f,f} | 0 | 0 | {f} | 4 | Pumpe 1, Pumpe 2, Pumpe 3, Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a914 | 1c4731e2-9139-46e4-9b81-4cbd69211be9 | MV_AS_E2M_AMEV1 |  |  | 3 | 2 |  | X | X | 1.2.2 = 3; 2.2.1 = 2; 3.1.1; 3.1.3 | [BAS] | [Description] | Anlagensteuerung | {f,f,f,f} | 0 | 0 | {f} | 3 | Erzeuger 1, Erzeuger 2, Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a915 | beaeef05-9db5-4605-aaff-38b10e836d71 | MV_AS_E3M_AMEV1 |  |  | 4 | 3 |  | X | X | 1.2.2 = 4; 2.2.1 = 3; 3.1.1; 3.1.3 | [BAS] | [Description] | Anlagensteuerung | {f,f,f,f} | 0 | 0 | {f} | 4 | Erzeuger 1, Erzeuger 2, Erzeuger 3, Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a916 | d2e8d92f-50f0-4e28-ba2f-e75a7f12ed73 | MV_AS_SEPCM_AMEV1 |  |  | 5 | 4 |  | X | X | 1.2.2 = 5; 2.2.1 = 4; 3.1.1; 3.1.3 | [BAS] | [Description] | Anlagensteuerung | {f,f,f,f} | 0 | 0 | {f} | 5 | Gebäudeschutz, Economy, Pre-Comfort, Comfort, Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a917 | 5efd2b72-c596-451c-b53b-368d2db7527f | MV_AS_AHKM_AMEV1 |  |  | 4 | 3 |  | X | X | 1.2.2 = 4; 2.2.1 = 3; 3.1.1; 3.1.3 | [BAS] | [Description] | Anlagensteuerung | {f,f,f,f} | 0 | 0 | {f} | 4 | Aus, Heizen, Kühlen, Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a918 | c2163994-fb4a-4cdb-be34-f542df085b55 | MV_AS_AV_2VM_AMEV1 |  |  | 4 | 3 |  | X | X | 1.2.2 = 4; 2.2.1 = 3; 3.1.1; 3.1.3 | [BAS] | [Description] | Anlagensteuerung | {f,f,f,f} | 0 | 0 | {f} | 4 | Aus, min Volumen, max Volumen, Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a919 | 755c468e-3871-44e6-8af1-69e2eaa23ae0 | MV_AS_JAL_AMEV1 |  |  | 12 |  |  | X | X | 1.2.2 = 12; 3.1.1; 3.1.3 | [BAS] | [Description] | Anlagensteuerung | {f,f,f,f} | 0 | 0 | {f} | 12 | Idle, Goto_Position, Stop, Up, Down, Step_Up, Step_down, Goto_Preset1, Goto_Preset2, Save_Preset1, Save_Preset2, Nutzereingriff | Idle | [10 empty] | {f} |  | 1 |  | >8
a920 | 78cf066d-58a3-4994-9bd8-846ccde31e60 | MV_AS_RWS_AMEV1 |  |  | 3 |  |  | X | X | 1.2.2 = 3; 3.1.1; 3.1.3 | [BAS] | [Description] | Anlagensteuerung RWS | {f,f,f,f} | 0 | 0 | {f} | 3 | Entriegeln;Verriegeln;Kurzzeitfreigabe | [11 empty] | {t} |  | 1 |  | >8
Betriebsartenschalter
a921 | aff63757-6e67-4a68-adbc-e22556307c9f | MV_BA_TUR_AMEV1 |  |  | 5 |  |  | X | X | 1.2.2 = 5; 3.1.1; 3.1.3 | [BAS] | [Description] | Betriebsartenschalter Türsystem | {f,f,f,f} | 0 | 0 | {f} | 5 | Dauer Zu;Dauer Auf;Einweg Austritt; Einweg Eintritt;Auto | [11 empty] | {t} |  | 1 |  | >8
Status
a922 | 2cc97084-bac4-4838-8857-c2af65a5baa1 | MV_STA_ALG_AMEV1 |  |  | n | ? |  | X | X | 1.2.2 = n; 2.2.1 = ?; 3.1.1; 3.1.3 | [BAS] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} |  | [nach Vorgabe] | [11 empty] | {f} |  | 1 |  | >8
a923 | e0081d7b-1c83-4153-a77a-5187938c46df | MV_STA_AEM_AMEV1 |  |  | 4 | 2 |  | X | X | 1.2.2 = 4; 2.2.1 = 2; 3.1.1; 3.1.3 | [BAS] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} | 4 | Hand-Aus, Hand-Ein, Auto-Ein, Auto-Aus | Auto-Aus |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a924 | e0eee284-e584-43ef-b9c9-639f39253b3a | MV_STA_ABYM_AMEV1 |  |  | 3 |  |  | X | X | 1.2.2 = 3; 3.1.1; 3.1.3 | [BAS] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} | 3 | Aus, Ein, Ein Bypass | [11 empty] | {f} |  | 1 |  | >8
a925 | 796a616c-0e40-4d50-97ce-9a9f0a97b156 | MV_STA_ASWM_AMEV1 |  |  | 3 |  |  | X | X | 1.2.2 = 3; 3.1.1; 3.1.3 | [BAS] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} | 3 | Aus, Sommer, Winter | [11 empty] | {f} |  | 1 |  | >8
a926 | 4d0378c8-14ef-4932-85a6-6158bc7f7fbe | MV_STA_AEF_AMEV1 |  |  | 3 |  |  | X | X | 1.2.2 = 3; 3.1.1; 3.1.3 | [BAS] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} | 3 | Aus, Ein, Fehler | [11 empty] | {f} |  | 1 |  | >8
a927 | 6c902c1a-fd11-462d-81cf-e862007ad666 | MV_STA_AES_AMEV1 |  |  | 3 |  |  | X | X | 1.2.2 = 3; 3.1.1; 3.1.3 | [BAS] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} | 3 | Aus, Ein, Störung | [11 empty] | {f} |  | 1 |  | >8
a928 | ccac615c-d67c-4c1b-9cd8-d3b7cc801ff0 | MV_STA_ASNF_AMEV1 |  |  | 3 |  |  | X | X | 1.2.2 = 3; 3.1.1; 3.1.3 | [BAS] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} | 3 | Aus, Schleichfahrt, Normalfahrt | [11 empty] | {f} |  | 1 |  | >8
a929 | 73e63cc2-65ea-4ff7-ad56-7ee4c00498cb | MV_STA_2n_AMEV1 |  |  | 3 |  |  | X | X | 1.2.2 = 3; 3.1.1; 3.1.3 | [BAS] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} | 3 | Aus, Stufe 1, Stufe 2 | [11 empty] | {f} |  | 1 |  | >8
a930 | fa4c24b6-0705-4c59-90a9-69f561a15702 | MV_STA_3n_AMEV1 |  |  | 4 |  |  | X | X | 1.2.2 = 4; 3.1.1; 3.1.3 | [BAS] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} | 4 | Aus, Stufe 1, Stufe 2, Stufe 3 | [11 empty] | {f} |  | 1 |  | >8
a931 | 0e04ff12-ac48-48d3-b611-ee92d4bcc024 | MV_STA_3P_AMEV1 |  |  | 3 |  |  | X | X | 1.2.2 = 3; 3.1.1; 3.1.3 | [BAS] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} | 3 | Pumpe 1, Pumpe 2, Pumpe 3 | [11 empty] | {f} |  | 1 |  | >8
a932 | c288856b-fc24-49e3-a761-661c894c4898 | MV_STA_3E_AMEV1 |  |  | 3 |  |  | X | X | 1.2.2 = 3; 3.1.1; 3.1.3 | [BAS] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} | 3 | Erzeuger 1, Erzeuger 2, Erzeuger 3 | [11 empty] | {f} |  | 1 |  | >8
a933 | 78c6b3c2-b64e-4622-9253-f090cd8eea40 | MV_STA_SEPC_AMEV1 |  |  | 4 |  |  | X | X | 1.2.2 = 4; 3.1.1; 3.1.3 | [BAS] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} | 4 | Gebäudeschutz, Economy, Pre-Comfort, Comfort | [11 empty] | {f} |  | 1 |  | >8
a934 | 92936a90-db59-4765-9850-f7f2a2d71baa | MV_STA_SSEPC_AMEV1 |  |  | 5 |  |  | X | X | 1.2.2 = 5; 3.1.1; 3.1.3 | [BAS] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} | 5 | Gebäudeschutz-Fenster, Gebäudeschutz-Zeitplan, Economy, Pre-Comfort, Comfort | [11 empty] | {f} |  | 1 |  | >8
a935 | a989c7f4-3c9d-4dec-bd75-e0687510d20c | MV_STA_G_AMEV1 |  |  | 4 |  |  | X | X | 1.2.2 = 4; 3.1.1; 3.1.3 | [BAS] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} | 4 | Witterungsschutz, Manuell Stellen, Sonnenautomatik, Thermoautomatik | [11 empty] | {f} |  | 1 |  | >8
a936 | c421083a-c8d6-47e1-8cb7-c81ade4948d1 | MV_STA_AHK_AMEV1 |  |  | 3 |  |  | X | X | 1.2.2 = 3; 3.1.1; 3.1.3 | [BAS] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} | 3 | Aus, Heizen, Kühlen | [11 empty] | {f} |  | 1 |  | >8
a937 | 3e246010-f841-4a63-bd0b-d8a8f6d5a7b2 | MV_STA_AV2_AMEV1 |  |  | 3 |  |  | X | X | 1.2.2 = 3; 3.1.1; 3.1.3 | [BAS] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} | 3 | Aus, min Volumen, max Volumen | [11 empty] | {f} |  | 1 |  | >8
a938 | f7ac735e-bc6e-4c0b-9472-55ce68df459f | MV_STA_TUR_AMEV1 |  |  | 5 | 2 |  | X | X | 1.2.2 = 5; 2.2.1 = 2; 3.1.1; 3.1.3 | [BAS] | [Description] | Betriebsart Türsystem (Status) | {f,f,f,f} | 0 | 0 | {f} | 5 | Dauer Zu;Dauer Auf;Einweg Austritt; Einweg Eintritt;Auto | Auto |  | 250 |  | Dauer Auf, Einweg Eintritt |  | {t,t,t} | Alarm | * | * | *** | {f} |  | 1 |  | >8
a939 | eabe8e01-9fac-4213-8fee-d5b5c5fc06fd | MV_STA_RWS_AMEV1 |  |  | 3 |  |  | X | X | 1.2.2 = 3; 3.1.1; 3.1.3 | [BAS] | [Description] | Betriebsart RWS (Status) | {f,f,f,f} | 0 | 0 | {f} | 3 | Entriegelt;Verriegelt;Kurzzeitfreigabe | Verriegelt | >Kurzzeitfreigabe | 250 |  | <>Verriegelt |  | {t,t,t} | Alarm | * | * | *** | {f} |  | 1 |  | >8
Handmeldung/Handschaltung
a940 | 984145d2-dec1-4579-8222-982152efd91a | MV_HD_AEM_AMEV1 |  |  | 3 | 2 |  | X | X | 1.2.2 = 3; 2.2.1 = 2; 3.1.1; 3.1.3 | [BAS] | [Description] | Handmeldung | {f,f,f,f} | 0 | 0 | {f} | 3 | Aus, Ein, Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a941 | d44d333d-bf86-4b54-9882-ec10bbd053ae | MV_HD_ASGM_AMEV1 |  |  | 3 | 2 |  | X | X | 1.2.2 = 3; 2.2.1 = 2; 3.1.1; 3.1.3 | [BAS] | [Description] | Handmeldung | {f,f,f,f} | 0 | 0 | {f} | 3 | Aus, Stellgröße, Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a942 | b831c9e1-27ad-4ed6-9a7c-c5382736f87d | MV_HD_A2nM_AMEV1 |  |  | 4 | 3 |  | X | X | 1.2.2 = 4; 2.2.1 = 3; 3.1.1; 3.1.3 | [BAS] | [Description] | Handmeldung | {f,f,f,f} | 0 | 0 | {f} | 4 | Aus, Stufe 1, Stufe 2 ,Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a943 | 76a6b2d4-6fb6-4ac4-9260-30e70d9c3dec | MV_HD_A2HDM_AMEV1 |  |  | 4 | 3 |  | X | X | 1.2.2 = 4; 2.2.1 = 3; 3.1.1; 3.1.3 | [BAS] | [Description] | Handmeldung | {f,f,f,f} | 0 | 0 | {f} | 4 | Aus, Zu, Auf ,Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a944 | 361bec3a-d669-47e6-a7c3-d5c9c1e31079 | MV_HD_AnM_AMEV1 |  |  | 3 | 2 |  | X | X | 1.2.2 = 3; 2.2.1 = 2; 3.1.1; 3.1.3 | [BAS] | [Description] | Handmeldung | {f,f,f,f} | 0 | 0 | {f} | 3 | Aus, Drehzahl-Vorgabe, Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a945 | 34598cdd-baf1-4d54-ab6f-98bb197ff982 | MV_RM_ZKA_AMEV1 |  |  | 3 | 2 |  | X | X | 1.2.2 = 3; 2.2.1 = 2; 3.1.1; 3.1.3 | [BAS] | [Description] | Rückmeldung | {f,f,f,f} | 0 | 0 | {f} | 3 | Zu, gekippt, Auf | Auf |  | [**] |  | <>Zu |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a946 | 7fa02b15-1d27-41ad-939e-c757568d7c7b | MV_ZAF_ETS_AMEV1 |  |  | n |  |  | X | X | 1.2.2 = n; 3.1.1; 3.1.3 | [BAS] | [Description] | Etagenstand | {f,f,f,f} | 0 | 0 | {f} | n | [U2,U2,E,1,2,3…] | [11 empty] | {f} |  | 1 |  | >8
|  | * B (Bauherr/Betreiber), P (GA-Planung), U (Ausführendes Unternehmen) | [8 empty] | Vorgabewert (Parametrierung) und Prüfwert | [9 empty] | ** passend definieren |  |  |  | 1 Nur wenn Ausführkontrolle über Intrinsic Alarming ausgeführt wird
[11 empty] | Prüfwert (systemintern erzeugter Wert) | [15 empty] | *Kann zur Prüfung beim 1:1 Tests herangezogen werden
*** gemäß Kapitel 4.4 einrichten
ENGLISH VERSION (Draft)
ObjSort + No. | UUID | Object Template Identifier | Comment | BACS FL entries (1.1.2) | BACS FL entries (1.2.2) | BACS FL entries (2.2.1) | BACS FL entries (2.2.2) | BACS FL entries (3.1.1) | BACS FL entries (3.1.3) | BACS FL entries (sections/columns) | Object_Name | Description | Application | Status_Flags | Event_State | Reliability | Out_Of_Service | Number_Of_States | State_Text | Relinquish_Default | Time_Delay | Notification_Class | Feedback_Value (nur MO) | Alarm_Values (nur MV) | Fault_Values (nur MV) | Event_Enable | Notify_Type | Event_Time_Stamps | Event_Message_Texts | Event_Message_Texts_Config | Event_Detection_Enable | Event_Algorithm_Inhibit(_Ref) | Time_Delay_Normal | Reliability_Evaluation_Inhibit | Current_Command_Priority | Last change in version
|  | PropSort | [8 empty] | a11 | a12 | 5 |  |  |  |  | b42 | b15 | b16 | c43 | c11 | c19 | c17 | c18 | c12 | c13 |  |  | c14 | c15 | c41¦c42 | c44
|  | Conformance Code | R | [7 empty] | R | W |  | R | R | W1 | W | R | W | W | W | W | R | W | W | W | W | R | R | W | W | RA | W | RX¦O | R22
|  | Basic spezification * | [8 empty] | B * | B | [6 empty] | B | B | P | B | B | B | B | B | B |  |  | B | B | P | P
|  | Detailed definition * | [8 empty] | P * | P | [6 empty] | P | P | P | P | P | P | P | P | P |  |  | P | P | P | P
|  | Implementation * | [8 empty] | X * | X |  | X | X | X | X | X | X | X | X | X | X | X | X | X | X |  |  | X | X | X | X | X | X
|  | Default value (parameterization) | [8 empty] | yes | yes |  | no | no | no | no | no | yes | yes | yes | yes | no | yes | yes | yes | yes | no | no | yes | yes | no | yes | no | no
Switch Command
a801 | 1eece5c2-0478-4a7d-a388-a2906022ddb9 | MO_SB_ASn_AMEV1 | Level n | 2+n |  |  | 2+n | X | X | 1.1.2 = 2+n; 2.2.4 = 2+n; 3.1.1; 3.1.3 | [UAK] | [Description] | Switching command System Switch Stage n | {f,f,f,f} | 0 | 0 | {f} | [2+n] | [Off, Level 1, Level n] | Off | [**] |  |  |  |  | {t,t,t}¹ | Alarm¹ | *¹ | *¹ | ***¹ | {t/f}¹ |  | 1¹ |  | >8
a802 | 6febdcfb-47aa-40fa-95e9-4edc49672d85 | MO_SB_2n_AMEV1 |  | 3 |  |  | 3 | X | X | 1.1.2 = 3; 2.2.4 = 3; 3.1.1; 3.1.3 | [UAK] | [Description] | Switching command Two-stage | {f,f,f,f} | 0 | 0 | {f} | 3 | Off, Level 1, Level 2 | Off | [60]¹ | 300¹ |  |  |  | {t,t,t}¹ | Alarm¹ | *¹ | *¹ | ***¹ | {t/f}¹ |  | 1¹ |  | >8
a803 | c7f5731d-e7d8-4ac9-b963-002edbe23ee5 | MO_SB_3n_AMEV1 |  | 4 |  |  | 4 | X | X | 1.1.2 = 4; 2.2.4 = 4; 3.1.1; 3.1.3 | [UAK] | [Description] | Switching command Three-stage | {f,f,f,f} | 0 | 0 | {f} | 4 | Off, Level 1, Level 2, Level 3 | Off | [60]¹ | 300¹ |  |  |  | {t,t,t}¹ | Alarm¹ | *¹ | *¹ | ***¹ | {t/f}¹ |  | 1¹ |  | >8
Plant switch
a901 | 267ded4b-eaf4-4ee5-8b89-f14f99851646 | MV_AS_M_AMEV1 |  |  | 3 | 2 |  | X | X | 1.2.2 = 3; 2.2.1 = 2; 3.1.1; 3.1.3 | [UAK] | [Description] | Plant control | {f,f,f,f} | 0 | 0 | {f} | 3 | [by default] | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a902 | 3f3ca156-5543-49fb-b8d8-774bdc96c929 | MV_GS_AEM_AMEV1 |  |  | 3 | 2 |  | X | X | 1.2.2 = 3; 2.2.1 = 2; 3.1.1; 3.1.3 | [UAK] | [Description] | Overall system control | {f,f,f,f} | 0 | 0 | {f} | 3 | Off, On, Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a903 | c2854dd0-f2a9-447d-972c-88877bce48b8 | MV_AS_AEM_AMEV1 |  |  | 3 | 2 |  | X | X | 1.2.2 = 3; 2.2.1 = 2; 3.1.1; 3.1.3 | [UAK] | [Description] | Plant control | {f,f,f,f} | 0 | 0 | {f} | 3 | Off, On, Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a904 | 158e4a23-6201-4554-b8ff-3e4e3a79acfc | MV_GS_A2nM_AMEV1 |  |  | 4 | 3 |  | X | X | 1.2.2 = 4; 2.2.1 = 3; 3.1.1; 3.1.3 | [UAK] | [Description] | Overall system control | {f,f,f,f} | 0 | 0 | {f} | 4 | Off, Level 1, Level 2, Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a905 | 59554960-0c8c-4a99-a45b-8dcc0941b141 | MV_AS_A2nM_AMEV1 |  |  | 4 | 3 |  | X | X | 1.2.2 = 4; 2.2.1 = 3; 3.1.1; 3.1.3 | [UAK] | [Description] | Plant control | {f,f,f,f} | 0 | 0 | {f} | 4 | Off, Level 1, Level 2, Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a906 | b52201b7-ae17-4ff8-af56-6d98ec30af64 | MV_AS_ADZM_AMEV1 |  |  | 3 | 2 |  | X | X | 1.2.2 = 3; 2.2.1 = 2; 3.1.1; 3.1.3 | [UAK] | [Description] | Plant control | {f,f,f,f} | 0 | 0 | {f} | 3 | Off, RPM, Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a907 | 4eeb4604-22ac-4130-ac17-be26f2a5d822 | MV_AS_AEBM_AMEV1 |  |  | 4 | 3 |  | X | X | 1.2.2 = 4; 2.2.1 = 3; 3.1.1; 3.1.3 | [UAK] | [Description] | Plant control | {f,f,f,f} | 0 | 0 | {f} | 4 | Off, On, On Bypass, Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a908 | 32532ddb-c336-4576-a381-c599fea37555 | MV_AS_ASWM_AMEV1 |  |  | 4 | 3 |  | X | X | 1.2.2 = 4; 2.2.1 = 3; 3.1.1; 3.1.3 | [UAK] | [Description] | Plant control | {f,f,f,f} | 0 | 0 | {f} | 4 | Off, Summer, Winter, Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a909 | db6d18e4-5ff4-43d9-b7f0-297e7a722fbd | MV_AS_ASNF_AMEV1 |  |  | 4 |  |  | X | X | 1.2.2 = 4; 3.1.1; 3.1.3 | [UAK] | [Description] | Plant control | {f,f,f,f} | 0 | 0 | {f} | 4 | Off, Creep driving, Normal driving, Auto | Off | [10 empty] | {f} |  | 1 |  | >8
a910 | 1bce8316-e0ba-4413-b5ee-5728f159036d | MV_AS_A2n_AMEV1 |  |  | 3 |  |  | X | X | 1.2.2 = 3; 3.1.1; 3.1.3 | [UAK] | [Description] | Plant control | {f,f,f,f} | 0 | 0 | {f} | 3 | Off, Level 1, Level 2 | Off | [10 empty] | {f} |  | 1 |  | >8
a911 | ab87b375-9283-4401-a29d-de78b7e07607 | MV_AS_A3n_AMEV1 |  |  | 4 |  |  | X | X | 1.2.2 = 4; 3.1.1; 3.1.3 | [UAK] | [Description] | Plant control | {f,f,f,f} | 0 | 0 | {f} | 4 | Off, Level 1, Level 2, Level 3 | Off | [10 empty] | {f} |  | 1 |  | >8
a912 | 479eabb3-19a6-49a3-8bbc-c12c4538673c | MV_AS_P2M_AMEV1 |  |  | 3 | 2 |  | X | X | 1.2.2 = 3; 2.2.1 = 2; 3.1.1; 3.1.3 | [UAK] | [Description] | Plant control | {f,f,f,f} | 0 | 0 | {f} | 3 | Pump 1, Pump 2, Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a913 | aea173d8-8859-4ea0-a14c-75cb2c40bd23 | MV_AS_P3M_AMEV1 |  |  | 4 | 3 |  | X | X | 1.2.2 = 4; 2.2.1 = 3; 3.1.1; 3.1.3 | [UAK] | [Description] | Plant control | {f,f,f,f} | 0 | 0 | {f} | 4 | Pump 1, Pump 2, Pump 3, Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a914 | 1c4731e2-9139-46e4-9b81-4cbd69211be9 | MV_AS_E2M_AMEV1 |  |  | 3 | 2 |  | X | X | 1.2.2 = 3; 2.2.1 = 2; 3.1.1; 3.1.3 | [UAK] | [Description] | Plant control | {f,f,f,f} | 0 | 0 | {f} | 3 | Producer 1, Producer 2, Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a915 | beaeef05-9db5-4605-aaff-38b10e836d71 | MV_AS_E3M_AMEV1 |  |  | 4 | 3 |  | X | X | 1.2.2 = 4; 2.2.1 = 3; 3.1.1; 3.1.3 | [UAK] | [Description] | Plant control | {f,f,f,f} | 0 | 0 | {f} | 4 | Producer 1, Producer 2, Producer 3, Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a916 | d2e8d92f-50f0-4e28-ba2f-e75a7f12ed73 | MV_AS_SEPCM_AMEV1 |  |  | 5 | 4 |  | X | X | 1.2.2 = 5; 2.2.1 = 4; 3.1.1; 3.1.3 | [UAK] | [Description] | Plant control | {f,f,f,f} | 0 | 0 | {f} | 5 | Building Protection, Economy, Pre-Comfort, Comfort, Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a917 | 5efd2b72-c596-451c-b53b-368d2db7527f | MV_AS_AHKM_AMEV1 |  |  | 4 | 3 |  | X | X | 1.2.2 = 4; 2.2.1 = 3; 3.1.1; 3.1.3 | [UAK] | [Description] | Plant control | {f,f,f,f} | 0 | 0 | {f} | 4 | Off, Heating, Cooling, Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a918 | c2163994-fb4a-4cdb-be34-f542df085b55 | MV_AS_AV_2VM_AMEV1 |  |  | 4 | 3 |  | X | X | 1.2.2 = 4; 2.2.1 = 3; 3.1.1; 3.1.3 | [UAK] | [Description] | Plant control | {f,f,f,f} | 0 | 0 | {f} | 4 | Off, Min volume, Max volume, Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a919 | 755c468e-3871-44e6-8af1-69e2eaa23ae0 | MV_AS_JAL_AMEV1 |  |  | 12 |  |  | X | X | 1.2.2 = 12; 3.1.1; 3.1.3 | [UAK] | [Description] | Plant control | {f,f,f,f} | 0 | 0 | {f} | 12 | Idle, Goto_Position, Stop, Up, Down, Step_Up, Step_down, Goto_Preset1, Goto_Preset2, Save_Preset1, Save_Preset2, User intervention | Idle | [10 empty] | {f} |  | 1 |  | >8
a920 | 78cf066d-58a3-4994-9bd8-846ccde31e60 | MV_AS_RWS_AMEV1 |  |  | 3 |  |  | X | X | 1.2.2 = 3; 3.1.1; 3.1.3 | [UAK] | [Description] | Escape route system control | {f,f,f,f} | 0 | 0 | {f} | 3 | Unlock; Lock; Short-term release | [11 empty] | {t} |  | 1 |  | >8
Mode switch
a921 | aff63757-6e67-4a68-adbc-e22556307c9f | MV_BA_TUR_AMEV1 |  |  | 5 |  |  | X | X | 1.2.2 = 5; 3.1.1; 3.1.3 | [UAK] | [Description] | Operating Mode Switch Door System | {f,f,f,f} | 0 | 0 | {f} | 5 | Duration Closed; Duration Open; One-way Exit; One-way Entry; Auto | [11 empty] | {t} |  | 1 |  | >8
Status
a922 | 2cc97084-bac4-4838-8857-c2af65a5baa1 | MV_STA_ALG_AMEV1 |  |  | n | ? |  | X | X | 1.2.2 = n; 2.2.1 = ?; 3.1.1; 3.1.3 | [UAK] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} |  | [by default] | [11 empty] | {f} |  | 1 |  | >8
a923 | e0081d7b-1c83-4153-a77a-5187938c46df | MV_STA_AEM_AMEV1 |  |  | 4 | 2 |  | X | X | 1.2.2 = 4; 2.2.1 = 2; 3.1.1; 3.1.3 | [UAK] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} | 4 | Hand-Off, Hand-On, Auto-On, Auto-Off | Auto-Off |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a924 | e0eee284-e584-43ef-b9c9-639f39253b3a | MV_STA_ABYM_AMEV1 |  |  | 3 |  |  | X | X | 1.2.2 = 3; 3.1.1; 3.1.3 | [UAK] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} | 3 | Off, On, One Bypass | [11 empty] | {f} |  | 1 |  | >8
a925 | 796a616c-0e40-4d50-97ce-9a9f0a97b156 | MV_STA_ASWM_AMEV1 |  |  | 3 |  |  | X | X | 1.2.2 = 3; 3.1.1; 3.1.3 | [UAK] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} | 3 | Off, Summer, Winter | [11 empty] | {f} |  | 1 |  | >8
a926 | 4d0378c8-14ef-4932-85a6-6158bc7f7fbe | MV_STA_AEF_AMEV1 |  |  | 3 |  |  | X | X | 1.2.2 = 3; 3.1.1; 3.1.3 | [UAK] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} | 3 | Off, On, Error | [11 empty] | {f} |  | 1 |  | >8
a927 | 6c902c1a-fd11-462d-81cf-e862007ad666 | MV_STA_AES_AMEV1 |  |  | 3 |  |  | X | X | 1.2.2 = 3; 3.1.1; 3.1.3 | [UAK] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} | 3 | Off, On, Fault | [11 empty] | {f} |  | 1 |  | >8
a928 | ccac615c-d67c-4c1b-9cd8-d3b7cc801ff0 | MV_STA_ASNF_AMEV1 |  |  | 3 |  |  | X | X | 1.2.2 = 3; 3.1.1; 3.1.3 | [UAK] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} | 3 | Off, Creep speed, Normal speed | [11 empty] | {f} |  | 1 |  | >8
a929 | 73e63cc2-65ea-4ff7-ad56-7ee4c00498cb | MV_STA_2n_AMEV1 |  |  | 3 |  |  | X | X | 1.2.2 = 3; 3.1.1; 3.1.3 | [UAK] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} | 3 | Off, Level 1, Level 2 | [11 empty] | {f} |  | 1 |  | >8
a930 | fa4c24b6-0705-4c59-90a9-69f561a15702 | MV_STA_3n_AMEV1 |  |  | 4 |  |  | X | X | 1.2.2 = 4; 3.1.1; 3.1.3 | [UAK] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} | 4 | Off, Level 1, Level 2, Level 3 | [11 empty] | {f} |  | 1 |  | >8
a931 | 0e04ff12-ac48-48d3-b611-ee92d4bcc024 | MV_STA_3P_AMEV1 |  |  | 3 |  |  | X | X | 1.2.2 = 3; 3.1.1; 3.1.3 | [UAK] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} | 3 | Pump 1, Pump 2, Pump 3 | [11 empty] | {f} |  | 1 |  | >8
a932 | c288856b-fc24-49e3-a761-661c894c4898 | MV_STA_3E_AMEV1 |  |  | 3 |  |  | X | X | 1.2.2 = 3; 3.1.1; 3.1.3 | [UAK] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} | 3 | Producer 1, Producer 2, Producer 3 | [11 empty] | {f} |  | 1 |  | >8
a933 | 78c6b3c2-b64e-4622-9253-f090cd8eea40 | MV_STA_SEPC_AMEV1 |  |  | 4 |  |  | X | X | 1.2.2 = 4; 3.1.1; 3.1.3 | [UAK] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} | 4 | Building Protection, Economy, Pre-Comfort, Comfort | [11 empty] | {f} |  | 1 |  | >8
a934 | 92936a90-db59-4765-9850-f7f2a2d71baa | MV_STA_SSEPC_AMEV1 |  |  | 5 |  |  | X | X | 1.2.2 = 5; 3.1.1; 3.1.3 | [UAK] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} | 5 | Building Protection Windows, Building Protection Schedule, Economy, Pre-Comfort, Comfort | [11 empty] | {f} |  | 1 |  | >8
a935 | a989c7f4-3c9d-4dec-bd75-e0687510d20c | MV_STA_G_AMEV1 |  |  | 4 |  |  | X | X | 1.2.2 = 4; 3.1.1; 3.1.3 | [UAK] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} | 4 | Weather Protection, Manual Adjustment, Automatic Sun, Thermal Automatic | [11 empty] | {f} |  | 1 |  | >8
a936 | c421083a-c8d6-47e1-8cb7-c81ade4948d1 | MV_STA_AHK_AMEV1 |  |  | 3 |  |  | X | X | 1.2.2 = 3; 3.1.1; 3.1.3 | [UAK] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} | 3 | Off, Heat, Cool | [11 empty] | {f} |  | 1 |  | >8
a937 | 3e246010-f841-4a63-bd0b-d8a8f6d5a7b2 | MV_STA_AV2_AMEV1 |  |  | 3 |  |  | X | X | 1.2.2 = 3; 3.1.1; 3.1.3 | [UAK] | [Description] | Status | {f,f,f,f} | 0 | 0 | {f} | 3 | Off, Min volume, Max volume | [11 empty] | {f} |  | 1 |  | >8
a938 | f7ac735e-bc6e-4c0b-9472-55ce68df459f | MV_STA_TUR_AMEV1 |  |  | 5 | 2 |  | X | X | 1.2.2 = 5; 2.2.1 = 2; 3.1.1; 3.1.3 | [UAK] | [Description] | Door System Operating mode (Status) | {f,f,f,f} | 0 | 0 | {f} | 5 | duration; duration; one-way exit; one-way entry; Auto | Auto |  | 250 |  | duration, |  | {t,t,t} | Alarm | * | * | *** | {f} |  | 1 |  | >8
a939 | eabe8e01-9fac-4213-8fee-d5b5c5fc06fd | MV_STA_RWS_AMEV1 |  |  | 3 |  |  | X | X | 1.2.2 = 3; 3.1.1; 3.1.3 | [UAK] | [Description] | Escape route system Operating mode (Status) | {f,f,f,f} | 0 | 0 | {f} | 3 | Unlocked; Locked; Short-term release | Locked | > Short-term release | 250 |  | One-way admission |  | {t,t,t} | Alarm | * | * | *** | {f} |  | 1 |  | >8
Manual signal/manual transmission
a940 | 984145d2-dec1-4579-8222-982152efd91a | MV_HD_AEM_AMEV1 |  |  | 3 | 2 |  | X | X | 1.2.2 = 3; 2.2.1 = 2; 3.1.1; 3.1.3 | [UAK] | [Description] | Local override message | {f,f,f,f} | 0 | 0 | {f} | 3 | Off, On, Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a941 | d44d333d-bf86-4b54-9882-ec10bbd053ae | MV_HD_ASGM_AMEV1 |  |  | 3 | 2 |  | X | X | 1.2.2 = 3; 2.2.1 = 2; 3.1.1; 3.1.3 | [UAK] | [Description] | Local override message | {f,f,f,f} | 0 | 0 | {f} | 3 | Off, Control Variable, Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a942 | b831c9e1-27ad-4ed6-9a7c-c5382736f87d | MV_HD_A2nM_AMEV1 |  |  | 4 | 3 |  | X | X | 1.2.2 = 4; 2.2.1 = 3; 3.1.1; 3.1.3 | [UAK] | [Description] | Local override message | {f,f,f,f} | 0 | 0 | {f} | 4 | Off, Level 1, Level 2 ,Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a943 | 76a6b2d4-6fb6-4ac4-9260-30e70d9c3dec | MV_HD_A2HDM_AMEV1 |  |  | 4 | 3 |  | X | X | 1.2.2 = 4; 2.2.1 = 3; 3.1.1; 3.1.3 | [UAK] | [Description] | Local override message | {f,f,f,f} | 0 | 0 | {f} | 4 | Off, Closed, Open ,Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a944 | 361bec3a-d669-47e6-a7c3-d5c9c1e31079 | MV_HD_AnM_AMEV1 |  |  | 3 | 2 |  | X | X | 1.2.2 = 3; 2.2.1 = 2; 3.1.1; 3.1.3 | [UAK] | [Description] | Local override message | {f,f,f,f} | 0 | 0 | {f} | 3 | Off, RPM Preset, Auto | Auto |  | 500 |  | <>Auto |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a945 | 34598cdd-baf1-4d54-ab6f-98bb197ff982 | MV_RM_ZKA_AMEV1 |  |  | 3 | 2 |  | X | X | 1.2.2 = 3; 2.2.1 = 2; 3.1.1; 3.1.3 | [UAK] | [Description] | Feedback | {f,f,f,f} | 0 | 0 | {f} | 3 | Closed, Tilted, On | Open |  | [**] |  | <>Closed |  | {t,t,t} | Alarm | * | * | *** | {t} |  | 1 |  | >8
a946 | 7fa02b15-1d27-41ad-939e-c757568d7c7b | MV_ZAF_ETS_AMEV1 |  |  | n |  |  | X | X | 1.2.2 = n; 3.1.1; 3.1.3 | [UAK] | [Description] | Floor indicator | {f,f,f,f} | 0 | 0 | {f} | n | [U2,U2,E,1,2,3...] | [11 empty] | {f} |  | 1 |  | >8
|  | * B (Builder/Operator), P (Planning), X (Executing Company) | [8 empty] | Default value (parameterization) and test value | [9 empty] | ** Define appropriately |  |  |  |  | 1 Only when execution control is performed via intrinsic alarming
[11 empty] | Test value (internally generated value) | [16 empty] | * Can be used for testing in the 1:1 test
*** Implementation according to Chapter 4.3

## 8.11 NC
ObjSort + LfdNr | UUID | Objekt-Template- Kennung | Kommentar | GA-FL Einträge (3.1.1) | GA-FL Einträge (3.1.3) | GA-FL Einträge (Abschnitte/Spalten) | Object_Name | Object_Identifier | Description | Priority | Ack_Required | Recipient_List | Letztmalige Änderung in Version
|  | PropSort |  |  |  |  | a11 | a71 | a12 | c20 | c21 | c22
|  | Conformance Code |  |  |  |  | RC | R | W | W | W | W
|  | Grundlegende Vorgabe * |  |  |  |  | B * | B | B | B | B | B
|  | Detailierte Festlegung * |  |  |  |  | P * | P | P | P | P | B
|  | Umsetzung * |  |  |  |  | U * | U | U | U | U | U
|  | Vorgabewert (Parametrierung) |  |  |  |  | ja | ja | ja | ja | ja | ja
b101 | dad1a77f-0ae8-4bdb-aa7a-66bb17ec81e0 | NC_GM_PSA_AMEV1 |  | X | X | 1.3.3; 3.1.1 | [BAS] | NC100 | Meldeklasse Gefahr Personen | {10,11,110} | {t,t,t} | [gemäß Vorgaben Recipient_List]
b102 | 31d0d24c-2022-45b5-8022-e7055de62462 | NC_GM_OSA_AMEV1 |  | X | X | 1.3.3; 3.1.1 | [BAS] | NC150 | Meldeklasse Gefahr Liegenschaft | {15,16,115} | {t,t,t} | [gemäß Vorgaben Recipient_List]
b103 | 4842f51e-d04b-40ad-a42a-fb1bcd527720 | NC_AM_GA_AMEV1 |  | X | X | 1.3.3; 3.1.1 | [BAS] | NC200 | Meldeklasse Alarm | {20,21,120} | {t,t,f} | [gemäß Vorgaben Recipient_List]
b104 | f85f5421-36ef-4393-95a7-a86dd5cf9b7b | NC_VAM_GA_AMEV1 |  | X | X | 1.3.3; 3.1.1 | [BAS] | NC250 | Meldeklasse Voralarm | {25,26,125} | {t,t,f} | [gemäß Vorgaben Recipient_List]
b105 | 62ae64a8-f3a6-4f79-8079-4582d7309f8c | NC_SM_GA_AMEV1 |  | X | X | 1.3.3; 3.1.1 | [BAS] | NC300 | Meldeklasse Störung | {30,31,130} | {t,t,f} | [gemäß Vorgaben Recipient_List]
b106 | 6505da0c-c559-4c10-9f7b-9345a3161d15 | NC_ANO_GA_AMEV1 |  | X | X | 1.3.3; 3.1.1 | [BAS] | NC350 | Meldeklasse Anormal | {35,36,135} | {f,f,f} | [gemäß Vorgaben Recipient_List]
b107 | db271fd5-6637-4ade-9594-baa915566b84 | NC_WM_GA_AMEV1 |  | X | X | 1.3.3; 3.1.1 | [BAS] | NC400 | Meldeklasse Wartung | {40,41,140} | {f,f,f} | [gemäß Vorgaben Recipient_List]
b108 | 65944290-b4b2-4c36-9296-5d0f12a0a666 | NC_WM_GAQ_AMEV1 |  | X | X | 1.3.3; 3.1.1 | [BAS] | NC425 | Meldeklasse Wartung (quittierbar) | {42,43,142} | {t,f,f} | [gemäß Vorgaben Recipient_List]
b109 | 09730c62-e7ab-4c65-82cf-c85566cb2749 | NC_RVM_GA_AMEV1 |  | X | X | 1.3.3; 3.1.1 | [BAS] | NC450 | Meldeklasse Revision | {45,46,145} | {f,f,f} | [gemäß Vorgaben Recipient_List]
b110 | e7e5a694-06df-484b-acbc-50aeeebd69b7 | NC_HD_GA_AMEV1 |  | X | X | 1.3.3; 3.1.1 | [BAS] | NC500 | Meldeklasse Handeingriff | {50,51,150} | {f,f,f} | [gemäß Vorgaben Recipient_List]
b111 | 85a6360e-d953-4de8-af39-92f4578a0fe5 | NC_SYS_GA_AMEV1 |  | X | X | 1.3.3; 3.1.1 | [BAS] | NC600 | Meldeklasse System | {60,61,160} | {t,f,f} | [gemäß Vorgaben Recipient_List]
b112 | 56fffc30-b61c-4a9d-9947-3ddb975d0537 | NC_TL_GA_AMEV1 |  | X | X | 1.3.3; 3.1.1 | [BAS] | NC700 | Meldeklasse Trend | {70,71,170} | {f,f,f} | [gemäß Vorgaben Recipient_List]
b113 | 5a9bc923-5a57-4314-bca6-6e1f7deb24c6 | NC_SO_GA_AMEV1 |  | X | X | 1.3.3; 3.1.1 | [BAS] | NC800 | Meldeklasse Sonstiges | {80,81,180} | {f,f,f} | [gemäß Vorgaben Recipient_List]
|  | * B (Bauherr/Betreiber), P (GA-Planung), U (Ausführendes Unternehmen) |  |  |  |  | Vorgabewert (Parametrierung) und Prüfwert
ENGLISH VERSION (Draft)
ObjSort + No. | UUID | Object Template Identifier | Comment | BACS FL entries (3.1.1) | BACS FL entries (3.1.3) | BACS FL entries (sections/columns) | Object_Name | Object_Identifier | Description | Priority | Ack_Required | Recipient_List | Last change in version
|  | PropSort |  |  |  |  | a11 | a71 | a12 | c20 | c21 | c22
|  | Conformance Code |  |  |  |  | RC | R | W | W | W | W
|  | Basic spezification * |  |  |  |  | B * | B | B | B | B | B
|  | Detailed definition * |  |  |  |  | P * | P | P | P | P | B
|  | Implementation * |  |  |  |  | X * | X | X | X | X | X
|  | Default value (parameterization) |  |  |  |  | yes | yes | yes | yes | yes | yes
b101 | dad1a77f-0ae8-4bdb-aa7a-66bb17ec81e0 | NC_GM_PSA_AMEV1 |  | X | X | 1.3.3; 3.1.1 | [UAK] | NC100 | Notification class Danger People | {10,11,110} | {t,t,t} | [according to specifications Recipient_List]
b102 | 31d0d24c-2022-45b5-8022-e7055de62462 | NC_GM_OSA_AMEV1 |  | X | X | 1.3.3; 3.1.1 | [UAK] | NC150 | Notification class Danger Property | {15,16,115} | {t,t,t} | [according to specifications Recipient_List]
b103 | 4842f51e-d04b-40ad-a42a-fb1bcd527720 | NC_AM_GA_AMEV1 |  | X | X | 1.3.3; 3.1.1 | [UAK] | NC200 | Notification class Alarm | {20,21,120} | {t,t,f} | [according to specifications Recipient_List]
b104 | f85f5421-36ef-4393-95a7-a86dd5cf9b7b | NC_VAM_GA_AMEV1 |  | X | X | 1.3.3; 3.1.1 | [UAK] | NC250 | Notification class Pre-alarm | {25,26,125} | {t,t,f} | [according to specifications Recipient_List]
b105 | 62ae64a8-f3a6-4f79-8079-4582d7309f8c | NC_SM_GA_AMEV1 |  | X | X | 1.3.3; 3.1.1 | [UAK] | NC300 | Notification class Fault | {30,31,130} | {t,t,f} | [according to specifications Recipient_List]
b106 | 6505da0c-c559-4c10-9f7b-9345a3161d15 | NC_ANO_GA_AMEV1 |  | X | X | 1.3.3; 3.1.1 | [UAK] | NC350 | Notification class Abnormal | {35,36,135} | {f,f,f} | [according to specifications Recipient_List]
b107 | db271fd5-6637-4ade-9594-baa915566b84 | NC_WM_GA_AMEV1 |  | X | X | 1.3.3; 3.1.1 | [UAK] | NC400 | Notification class Maintenance | {40,41,140} | {f,f,f} | [according to specifications Recipient_List]
b108 | 65944290-b4b2-4c36-9296-5d0f12a0a666 | NC_WM_GAQ_AMEV1 |  | X | X | 1.3.3; 3.1.1 | [UAK] | NC425 | Notification class Maintenance (can be acknowledged) | {42,43,142} | {t,f,f} | [according to specifications Recipient_List]
b109 | 09730c62-e7ab-4c65-82cf-c85566cb2749 | NC_RVM_GA_AMEV1 |  | X | X | 1.3.3; 3.1.1 | [UAK] | NC450 | Notification class Revision | {45,46,145} | {f,f,f} | [according to specifications Recipient_List]
b110 | e7e5a694-06df-484b-acbc-50aeeebd69b7 | NC_HD_GA_AMEV1 |  | X | X | 1.3.3; 3.1.1 | [UAK] | NC500 | Notification class Manual intervention | {50,51,150} | {f,f,f} | [according to specifications Recipient_List]
b111 | 85a6360e-d953-4de8-af39-92f4578a0fe5 | NC_SYS_GA_AMEV1 |  | X | X | 1.3.3; 3.1.1 | [UAK] | NC600 | Notification class System | {60,61,160} | {t,f,f} | [according to specifications Recipient_List]
b112 | 56fffc30-b61c-4a9d-9947-3ddb975d0537 | NC_TL_GA_AMEV1 |  | X | X | 1.3.3; 3.1.1 | [UAK] | NC700 | Notification class Trend | {70,71,170} | {f,f,f} | [according to specifications Recipient_List]
b113 | 5a9bc923-5a57-4314-bca6-6e1f7deb24c6 | NC_SO_GA_AMEV1 |  | X | X | 1.3.3; 3.1.1 | [UAK] | NC800 | Notification class Miscellaneous | {80,81,180} | {f,f,f} | [according to specifications Recipient_List]
|  | * B (Builder/Operator), P (Planning), X (Executing Company) |  |  |  |  | Default value (parameterization) and test value

## 8.12 SCH
ObjSort + LfdNr | UUID | Objekt-Template- Kennung | Kommentar | GA-FL Einträge (1.3.1) | GA-FL Einträge (3.1.1) | GA-FL Einträge (3.1.3) | GA-FL Einträge (Abschnitte/Spalten) | Object_Name | Description | Verwendung | Effective_Period | Weekly_Schedule | Exception_Schedule | Schedule_Default | List_Of_Object_Property_References | Priority_For_Writing | Status_Flags | Reliability | Out_Of_Service | Notification_Class | Event_Enable | Event_State | Notify_Type | Event_Time_Stamps | Event_Message_Texts | Event_Message_Texts_Config | Event_Detection_Enable | Reliability_Evaluation_Inhibit | Letztmalige Änderung in Version
|  | PropSort | [5 empty] | a11 | a12 |  | e12 | e13 | e14 | e15 | e71 | b18 |  |  |  | c11 | c12 |  | c13 |  |  | c14 | c15
|  | Conformance Code | [5 empty] | RC | W |  | W | W | W | W | W | W | R | W1 | W | W | W | W | W | R | R | W | W | RX¦O
|  | Grundlegende Vorgabe * | [5 empty] | B * | B |  | B | B | B | B | P | B |  |  |  | B | B |  | B |  |  | B | B
|  | Detailierte Festlegung * | [5 empty] | P * | P |  | P | B | B | P | P | P |  |  |  | P | P |  | P |  |  | P | P
|  | Umsetzung * | [5 empty] | U * | U |  | U | U | U | U | U | U | U | U | U | U | U | U | U |  |  | U | U | U
|  | Vorgabewert (Parametrierung) | [5 empty] | ja | ja |  | ja | ja | ja | ja | ja | ja | nein | nein | nein | ja | ja | nein | ja | nein | nein | ja | ja | nein
d201 | 08d6e8ac-2195-44bd-81f2-163736a7d3ac | SCH_BN_AMEV1 |  | X | X | X | 1.3.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Zeitplan (binär) |  |  |  | inactive | nicht leer | 13 | {f,f,f,f} | 0 | {f} | 300 | {f,t,t} | 0 | Alarm | * | * |  | {t}
d202 | 8c4e2da1-ecd5-4ba9-a4c9-31c6780eb7e0 | SCH_AN_AMEV1 |  | X | X | X | 1.3.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Zeitplan (analog) |  |  |  | [<>0] | nicht leer | 13 | {f,f,f,f} | 0 | {f} | 300 | {f,t,t} | 0 | Alarm | * | * |  | {t}
d203 | fb3ce14b-ffeb-4162-a456-65b69e50ffc0 | SCH_MS_AMEV1 |  | X | X | X | 1.3.1; 3.1.1; 3.1.3 | [BAS] | [Description] | Zeitplan (mehrstufig) |  |  |  |  | nicht leer | 13 | {f,f,f,f} | 0 | {f} | 300 | {f,t,t} | 0 | Alarm | * | * | *** | {t}
|  | * B (Bauherr/Betreiber), P (GA-Planung), U (Ausführendes Unternehmen) | [5 empty] | Vorgabewert (Parametrierung) und Prüfwert | [14 empty] | * Kann beim 1:1 Test benutzt werden
[8 empty] | Prüfwert (systemintern erzeugter Wert) | [15 empty] | *** gemäß Kapitel 4.4 einrichten
ENGLISH VERSION (Draft)
ObjSort + No. | UUID | Object Template Identifier | Comment | BACS FL entries (1.3.1) | BACS FL entries (3.1.1) | BACS FL entries (3.1.3) | BACS FL entries (sections/columns) | Object_Name | Description | Application | Effective_Period | Weekly_Schedule | Exception_Schedule | Schedule_Default | List_Of_Object_Property_References | Priority_For_Writing | Status_Flags | Reliability | Out_Of_Service | Notification_Class | Event_Enable | Event_State | Notify_Type | Event_Time_Stamps | Event_Message_Texts | Event_Message_Texts_Config | Event_Detection_Enable | Reliability_Evaluation_Inhibit | Last change in version
|  | PropSort | [5 empty] | a11 | a12 |  | e12 | e13 | e14 | e15 | e71 | b18 |  |  |  | c11 | c12 |  | c13 |  |  | c14 | c15
|  | Conformance Code | [5 empty] | RC | W |  | W | W | W | W | W | W | R | W1 | W | W | W | W | W | R | R | W | W | RX¦O
|  | Basic spezification * | [5 empty] | B * | B |  | B | B | B | B | P | B |  |  |  | B | B |  | B |  |  | B | B
|  | Detailed definition * | [5 empty] | P * | P |  | P | B | B | P | P | P |  |  |  | P | P |  | P |  |  | P | P
|  | Implementation * | [5 empty] | X * | X |  | X | X | X | X | X | X | X | X | X | X | X | X | X |  |  | X | X | X
|  | Default value (parameterization) | [5 empty] | yes | yes |  | yes | yes | yes | yes | yes | yes | no | no | no | yes | yes | no | yes | no | no | yes | yes | no
d201 | 08d6e8ac-2195-44bd-81f2-163736a7d3ac | SCH_BN_AMEV1 |  | X | X | X | 1.3.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Schedule (binary) |  |  |  | inactive | not empty | 13 | {f,f,f,f} | 0 | {f} | 300 | {f,t,t} | 0 | Alarm | * | * |  | {t}
d202 | 8c4e2da1-ecd5-4ba9-a4c9-31c6780eb7e0 | SCH_AN_AMEV1 |  | X | X | X | 1.3.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Schedule (analogue) |  |  |  | [<>0] | not empty | 13 | {f,f,f,f} | 0 | {f} | 300 | {f,t,t} | 0 | Alarm | * | * |  | {t}
d203 | fb3ce14b-ffeb-4162-a456-65b69e50ffc0 | SCH_MS_AMEV1 |  | X | X | X | 1.3.1; 3.1.1; 3.1.3 | [UAK] | [Description] | Schedule (multistate) |  |  |  |  | not empty | 13 | {f,f,f,f} | 0 | {f} | 300 | {f,t,t} | 0 | Alarm | * | * | *** | {t}
|  | * B (Builder/Operator), P (Planning), X (Executing Company) | [5 empty] | Default value (parameterization) and test value | [13 empty] | * Can be used for testing in the 1:1 test
[8 empty] | Test value (internally generated value) | [12 empty] | *** Implementation according to Chapter 4.3

## 8.13 SV
ObjSort + LfdNr | UUID | Objekt-Template- Kennung | Kommentar | GA-FL Einträge (1.3.5) | GA-FL Einträge (3.1.1) | GA-FL Einträge (3.1.3) | GA-FL Einträge (Bemerkung, 4) | GA-FL Einträge (Abschnitte/Spalten) | Object_Name | Description | Verwendung | Node_Type | Node_Subtype | Subordinate_List | Letztmalige Änderung in Version
|  | PropSort | [6 empty] | a11 | a12 |  | x11 | x12 | x13
|  | Conformance Code | [6 empty] | RC | W |  | R | R | R
|  | Grundlegende Vorgabe * | [6 empty] | B * | B |  | B | B | B
|  | Detailierte Festlegung * | [6 empty] | P * | P |  | P | P | P
|  | Umsetzung * | [6 empty] | U * | U |  | U | U | U
|  | Vorgabewert (Parametrierung) | [6 empty] | ja | ja |  | ja | ja | ja
x101 | 57321d29-fd28-480e-b834-e058846cd97b | SV_ANL_AMEV1 |  | X | X | X | SV-ANL | 1.3.5 + [Bemerkung] SV-ANL; 3.1.1; 3.1.3 | [BAS] | [Description] | Anlage | SYSTEM | ANLAGE-Template-Kennung (AMEV oder Projekt) | Array der Objekt-Identifier (siehe Bibliothek 3)
x102 | 00ad872d-5cee-4fa3-a059-c5cbdb68821b | SV_BGP_AMEV1 |  | X | X | X | SV-BGP | 1.3.5 + [Bemerkung] SV-BGP; 3.1.1; 3.1.3 | [BAS] | [Description] | Baugruppe | SUBSYSTEM | BAUGRUPPE-Template-Kennung (AMEV oder Projekt) | Array der Objekt-Identifier (siehe Bibliothek 3)
x103 | f12bd688-687c-49dd-b027-09f44f3c7296 | SV_AGG_AMEV1 |  | X | X | X | SV-AGG | 1.3.5 + [Bemerkung] SV-AGG; 3.1.1; 3.1.3 | [BAS] | [Description] | Aggregat | EQUIPMENT | AGGREGATE-Template-Kennung (AMEV oder Projekt) | Array der Objekt-Identifier (siehe Bibliothek 3)
|  | * B (Bauherr/Betreiber), P (GA-Planung), U (Ausführendes Unternehmen) | [6 empty] | Vorgabewert (Parametrierung) und Prüfwert
ENGLISH VERSION (Draft)
ObjSort + No. | UUID | Object Template Identifier | Comment | BACS FL entries (1.3.5) | BACS FL entries (3.1.1) | BACS FL entries (3.1.3) | BACS FL entries (Remarks, 4) | BACS FL entries (sections/columns) | Object_Name | Description | Application | Node_Type | Node_Subtype | Subordinate_List | Last change in version
|  | PropSort | [6 empty] | a11 | a12 |  | x11 | x12 | x13
|  | Conformance Code | [6 empty] | RC | W |  | R | R | R
|  | Basic spezification * | [6 empty] | B * | B |  | B | B | B
|  | Detailed definition * | [6 empty] | P * | P |  | P | P | P
|  | Implementation * | [6 empty] | X * | X |  | X | X | X
|  | Default value (parameterization) | [6 empty] | yes | yes |  | yes | yes | yes
x101 | 57321d29-fd28-480e-b834-e058846cd97b | SV_ANL_AMEV1 |  | X | X | X | SV-ANL | 1.3.5 + [Remarks] SV-ANL; 3.1.1; 3.1.3 | [UAK] | [Description] | Plant | SYSTEM | Plant Template Identifier (AMEV or project) | Array of object identifiers (see Library 3)
x102 | 00ad872d-5cee-4fa3-a059-c5cbdb68821b | SV_BGP_AMEV1 |  | X | X | X | SV-BGP | 1.3.5 + [Remarks] SV-BGP; 3.1.1; 3.1.3 | [UAK] | [Description] | Assembly | SUBSYSTEM | Assembly Template Idenitifier (AMEV or project) | Array of object identifiers (see Library 3)
x103 | f12bd688-687c-49dd-b027-09f44f3c7296 | SV_AGG_AMEV1 |  | X | X | X | SV-AGG | 1.3.5 + [Remarks] SV-AGG; 3.1.1; 3.1.3 | [UAK] | [Description] | Aggregate | EQUIPMENT | Aggregate Template Identifier (AMEV or project) | Array of object identifiers (see Library 3)
|  | * B (Builder/Operator), P (Planning), X (Executing Company) | [6 empty] | Default value (parameterization) and test value

## 8.14 TL
ObjSort + LfdNr | UUID | Objekt-Template- Kennung | Kommentar | GA-FL Einträge (1.3.4) | GA-FL Einträge (3.1.1) | GA-FL Einträge (3.1.3) | GA-FL Einträge (Abschnitte/Spalten) | Object_Name | Description | Verwendung | Enable | Log_DeviceObjectProperty | Log_Interval | COV_Resubscription_Interval4 | Client_COV_Increment | Stop_When_Full | Buffer_Size | Logging_Type | Trigger | Status_Flags | Reliability | Notification_Threshold | Event_State | Notification_Class | Event_Enable | Notify_Type | Event_Time_Stamps | Event_Message_Texts_Config | Event_Detection_Enable | Letztmalige Änderung in Version
|  | PropSort | [5 empty] | a11 | a12 |  | d11 | d12 | d13 | d14 | d15 | d16 | d17 | d18 | d19 |  |  | d20 |  | c11 | c12 | c13 |  | c14 | c15
|  | Conformance Code | [5 empty] | RC | W | [10 empty] | R | W1 | W | R | W | W | W | R | W | W | bar: d11 to d19
|  | Grundlegende Vorgabe * | [5 empty] | B * | B | [12 empty] | B |  | B | B | B |  | B | B | bar: d11 to d19
|  | Detailierte Festlegung * | [5 empty] | P * | P | [12 empty] | P |  | P | P | P |  | P | P | bar: d11 to d19
|  | Umsetzung * | [5 empty] | U * | U | [10 empty] | U | U | U | U | U | U | U |  | U | U | bar: d11 to d19
|  | Vorgabewert (Parametrierung) | [5 empty] | ja | ja | [10 empty] | nein | nein | ja | nein | ja | ja | ja | nein | ja | ja | bar: d11 to d19
c101 | 2fa36049-7613-4315-aaf8-d6ab9a1cdae7 | TL_AN_P_AMEV1 |  | X | X | X | 1.3.4; 3.1.1; 3.1.3 | [BAS] | [Description] | Datenaufzeichnung analog Polling | {t} | referenziertes Objekt | 900 | 86400 |  | false | 1000 | POLLING | {f} | {f,f,f,f} | 0 | [400] | 0 | 700 | to-normal | event | * | leer | {t}
c102 | ab14337c-ce7a-4f84-9110-d137134910b6 | TL_AN_C_AMEV1 |  | X | X | X | 1.3.4; 3.1.1; 3.1.3 | [BAS] | [Description] | Datenaufzeichnung analog COV | {t} | referenziertes Objekt |  | 86400 | NULL | false | 1000 | COV | {f} | {f,f,f,f} | 0 | [400] | 0 | 700 | to-normal | event | * | leer | {t}
c103 | 040fe42c-7c56-4bc8-a007-a3f5a310d300 | TL_AN_ZW_AMEV1 |  | X | X | X | 1.3.4; 3.1.1; 3.1.3 | [BAS] | [Description] | Datenaufzeichnung analog Zählwerte | {t} | referenziertes Objekt | [900] | 86400 |  | false | 1000 | POLLING | {f} | {f,f,f,f} | 0 | [400] | 0 | 700 | to-normal | event | * | leer | {t}
c104 | e0ac84f5-da65-4825-9d02-89915e180201 | TL_BN_AMEV1 |  | X | X | X | 1.3.4; 3.1.1; 3.1.3 | [BAS] | [Description] | Datenaufzeichnung binär | {t} | referenziertes Objekt |  | 86400 | NULL | false | 1000 | COV | {f} | {f,f,f,f} | 0 | [400] | 0 | 700 | to-normal | event | * | leer | {t}
c105 | f485d0a1-f49e-49e2-8d61-bf8272825761 | TL_MS_AMEV1 |  | X | X | X | 1.3.4; 3.1.1; 3.1.3 | [BAS] | [Description] | Datenaufzeichnung mehrstufig | {t} | referenziertes Objekt |  | 86400 | NULL | false | 1000 | COV | {f} | {f,f,f,f} | 0 | [400] | 0 | 700 | to-normal | event | * | leer | {t}
|  | * B (Bauherr/Betreiber), P (GA-Planung), U (Ausführendes Unternehmen) | [5 empty] | Vorgabewert (Parametrierung) und Prüfwert |  |  | d14: 4COV_Resubscription_Interval: nur für TrendLogs auf Fremd-Controller
* Kann zur Prüfung Buffer_Ready Meldung benutzt werden
ENGLISH VERSION (Draft)
ObjSort + No. | UUID | Object Template Identifier | Comment | BACS FL entries (1.3.4) | BACS FL entries (3.1.1) | BACS FL entries (3.1.3) | BACS FL entries (sections/columns) | Object_Name | Description | Application | Enable | Log_DeviceObjectProperty | Log_Interval | COV_Resubscription_Interval4 | Client_COV_Increment | Stop_When_Full | Buffer_Size | Logging_Type | Trigger | Status_Flags | Reliability | Notification_Threshold | Event_State | Notification_Class | Event_Enable | Notify_Type | Event_Time_Stamps | Event_Message_Texts_Config | Event_Detection_Enable | Last change in version
|  | PropSort | [5 empty] | a11 | a12 |  | d11 | d12 | d13 | d14 | d15 | d16 | d17 | d18 | d19 |  |  | d20 |  | c11 | c12 | c13 |  | c14 | c15
|  | Conformance Code | [5 empty] | RC | W | [10 empty] | R | W1 | W | R | W | W | W | R | W | W | bar: d11 to d19
|  | Basic spezification * | [5 empty] | B * | B | [12 empty] | B |  | B | B | B |  | B | B | bar: d11 to d19
|  | Detailed definition * | [5 empty] | P * | P | [12 empty] | P |  | P | P | P |  | P | P | bar: d11 to d19
|  | Implementation * | [5 empty] | X * | X | [10 empty] | X | X | X | X | X | X | X |  | X | X | bar: d11 to d19
|  | Default value (parameterization) | [5 empty] | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | no | no | yes | no | yes | yes | yes | no | yes | yes
c101 | 2fa36049-7613-4315-aaf8-d6ab9a1cdae7 | TL_AN_P_AMEV1 |  | X | X | X | 1.3.4; 3.1.1; 3.1.3 | [UAK] | [Description] | Data recording analogous POLLING | {t} | referenced object | 900 | 86400 |  | false | 1000 | POLLING | {f} | {f,f,f,f} | 0 | [400] | 0 | 700 | to-normal | event | * | no entry | {t}
c102 | ab14337c-ce7a-4f84-9110-d137134910b6 | TL_AN_C_AMEV1 |  | X | X | X | 1.3.4; 3.1.1; 3.1.3 | [UAK] | [Description] | Data recording analogous COV | {t} | referenced object |  | 86400 | NULL | false | 1000 | COV | {f} | {f,f,f,f} | 0 | [400] | 0 | 700 | to-normal | event | * | no entry | {t}
c103 | 040fe42c-7c56-4bc8-a007-a3f5a310d300 | TL_AN_ZW_AMEV1 |  | X | X | X | 1.3.4; 3.1.1; 3.1.3 | [UAK] | [Description] | Data recording analogous Counter | {t} | referenced object | [900] | 86400 |  | false | 1000 | POLLING | {f} | {f,f,f,f} | 0 | [400] | 0 | 700 | to-normal | event | * | no entry | {t}
c104 | e0ac84f5-da65-4825-9d02-89915e180201 | TL_BN_AMEV1 |  | X | X | X | 1.3.4; 3.1.1; 3.1.3 | [UAK] | [Description] | Data Recording Binary | {t} | referenced object |  | 86400 | NULL | false | 1000 | COV | {f} | {f,f,f,f} | 0 | [400] | 0 | 700 | to-normal | event | * | no entry | {t}
c105 | f485d0a1-f49e-49e2-8d61-bf8272825761 | TL_MS_AMEV1 |  | X | X | X | 1.3.4; 3.1.1; 3.1.3 | [UAK] | [Description] | Data Recording Multistate | {t} | referenced object |  | 86400 | NULL | false | 1000 | COV | {f} | {f,f,f,f} | 0 | [400] | 0 | 700 | to-normal | event | * | no entry | {t}
|  | * B (Builder/Operator), P (Planning), X (Executing Company) | [5 empty] | Default value (parameterization) and test value |  |  | d14: 4COV_Resubscription_Interval: only for TrendLogs on third-party controllers
* Can be used to check Buffer_Ready report

## 15 Funktionsbereich
Kennung Property | Funktionsbereich | Kennung Objekttyp
a. | Adressierung | ---
b. | Datenaustausch | B
c. | Alarm- und Eventmanagement | C
d. | Datenaufzeichnung | D
e. | Zeitmanagement | E
f. | Regler | F
g. - w. | nicht belegt (Reserveplatz für Erweiterungen) | G - W
x. | Struktur | X
y. | Geräte- und Netzwerk-Management | Y

## 16 ZuständKennung
Kennbuchstabe | Zuständigkeitsbereich: Beispiel | Ziffernblock
B = Bauherr, Betrieb | Adressierung, Beschreibung, Priorität, Zustandstext, Sollwert, Schaltzeit, Kalender, mind. BACnet Protokoll Revision | B = 11 - 39
P = GA-Planung | Montageort, Grenzwert, physikalische Einheit, Vorgabewert, Aufzeichnungsintervall, Reglertyp | P = 41 - 69
U = Ausführendes Unternehmen | Objekt-Instanz, Vendor-Information, Software-Information, Netzwerk-Einstellung | U = 71 - 99

## 17 ZuständigTab
18 Zuständigkeitstabelle
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Ges.Nr. | Objekttyp | Obj.Nr. | Property | ConfCode | PropSort
Nr | Nr | Fkt.Bereich | Property | Prop | Zust * | b1 | b2 | b3 | b4 | b5 | b6 | b7 | b8 | b9 | c1 | c2 | d1 | e1 | e2 | f1 | x1 | y1 | y2 | 1 | AI | 1 | Objekt_Template | ConfCode
ges. | Ber. | Name |  | Sort | * | AI | AO | AV | BI | BO | BV | MI | MO | MV | NC | EE | TL | CAL | SCH | LP | SV | DEV | FIL | 2 | AI | 2 | Object_Name | R | a11
1 | 1 | a. Adressierung | Object_Name | a11 | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | 3 | AI | 3 | Description | W | a12
2 | 2 |  | Description | a12 | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | 4 | AI | 4 | Description Präfix
3 | 3 |  | Object_Type | a13 | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B | 5 | AI | 5 | Zweck
4 | 4 |  | Object_Identifier | a71 | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | 6 | AI | 6 | Device_Type | R
5 | 1 | b. Daten-austausch | Units | Sort: b11; *: B; AI: B; AO: B; AV: B | 8 | AI | 8 | Event_State | R
6 | 2 |  | Polarity | Sort: b12; *: B; BI: B; BO: B | 9 | AI | 9 | Reliability | R
7 | 3 |  | Inactive_Text | Sort: b13; *: B; BI: B; BO: B; BV: B | 10 | AI | 10 | Out_Of_Service | W
8 | 4 |  | Active_Text | Sort: b14; *: B; BI: B; BO: B; BV: B | 11 | AI | 11 | Update_Interval | R
9 | 5 |  | State_Text | Sort: b15; *: B; MI: B; MO: B; MV: B | 12 | AI | 12 | Units | W | b11
10 | 6 |  | Relinquish_Default | Sort: b16; *: B; AO: B; AV: B; BO: B; BV: B; MO: B; MV: B | 13 | AI | 13 | Min_Pres_Value | R | c45
11 | 7 |  | COV_Increment | Sort: b17; *: B; AI: B; AO: B; AV: B; LP: B | 14 | AI | 14 | Max_Pres_Value | R | c46
12 | 8 |  | Priority_For_Writing | Sort: b18; *: B; SCH: B; LP: B | 15 | AI | 15 | Resolution | R | b41
13 | 9 |  | Resolution | Sort: b41; *: P; AI: P; AO: P | 16 | AI | 16 | COV_Increment | W | b17
14 | 10 |  | Number_Of_States | Sort: b42; *: P; MI: P; MO: P; MV: P | 17 | AI | 17 | Time_Delay | W | c43
15 | 11 |  | Minimum_Off_Time | Sort: b43; *: P; BO: P; BV: P | 18 | AI | 18 | Notification_Class | W | c11
16 | 12 |  | Minimum_On_Time | Sort: b44; *: P; BO: P; BV: P | 19 | AI | 19 | Low_Limit | W | c47
17 | 1 | c. Alarm- und Event-management | Notification_Class | c11 | B | B | B | B | B | B | B | B | B | B | B | B | B |  | B |  |  |  |  | 20 | AI | 20 | High_Limit | W | c48
18 | 2 |  | Event_Enable | c12 | B | B | B | B | B | B | B | B | B | B |  | B | B |  | B |  |  |  |  | 21 | AI | 21 | Deadband | W | c50
19 | 3 |  | Notify_Type | c13 | B | B | B | B | B | B | B | B | B | B |  | B | B |  | B |  |  |  |  | 22 | AI | 22 | Limit_Enable | W | c49
20 | 4 |  | Event_Message_Texts_Config | c14 | B | B | B | B | B | B | B | B | B | B |  | B | B |  | B |  |  |  |  | 23 | AI | 23 | Event_Enable | W | c12
21 | 5 |  | Event_Detection_Enable | c15 | B | B | B | B | B | B | B | B | B | B |  | B | B |  | B |  |  |  |  | 24 | AI | 24 | Acked_Transitions | R
22 | 6 |  | Alarm_Value | Sort: c16; *: B; BI: B; BV: B | 25 | AI | 25 | Notify_Type | W | c13
23 | 7 |  | Alarm_Values | Sort: c17; *: B; MI: B; MV: B | 26 | AI | 26 | Event_Time_Stamps | R
24 | 8 |  | Fault_Values | Sort: c18; *: B; MI: B; MV: B | 27 | AI | 27 | Event_Message_Texts | R
25 | 9 |  | Feedback_Value | Sort: c19; *: B; BO: B; MO: B | 28 | AI | 28 | Event_Message_Texts_Config | W | c14
26 | 10 |  | Priority | Sort: c20; *: B; NC: B | 29 | AI | 29 | Event_Detection_Enable | W | c15
27 | 11 |  | Ack_Required | Sort: c21; *: B; NC: B | 30 | AI | 30 | Event_Algorithm_Inhibit(_Ref) | R | c42
28 | 12 |  | Recipient_List | Sort: c22; *: B; NC: B | 31 | AI | 31 | Time_Delay_Normal | W | c44
29 | 13 |  | Event_Type | Sort: c23; *: B; EE: B | 32 | AI | 32 | Reliability_Evaluation_Inhibit | R
30 | 14 |  | Event_Parameters | Sort: c24; *: B; EE: B | 33 | AI | 33 | Property_List | R
31 | 15 |  | Event_Algorithm_Inhibit | c41 | P | P | P | P | P | P | P | P | P | P |  | P | [7 empty] | 34 | AO_AV | 1 | Objekt_Template | ConfCode
32 | 16 |  | Event_Algorithm_Inhibit_Ref | c42 | P | P | P | P | P | P | P | P | P | P |  | P | [7 empty] | 35 | AO_AV | 2 | Object_Name | R | a11
33 | 17 |  | Time_Delay | c43 | P | P | P | P | P | P | P | P | P | P | [5 empty] | P |  |  |  | 36 | AO_AV | 3 | Description | W | a12
34 | 18 |  | Time_Delay_Normal | c44 | P | P | P | P | P | P | P | P | P | P |  | P |  |  |  | P |  |  |  | 37 | AO_AV | 4 | Description Präfix
35 | 19 |  | Min_Pres_Value | Sort: c45; *: P; AI: P; AO: P; AV: P | 38 | AO_AV | 5 | Zweck
36 | 20 |  | Max_Pres_Value | Sort: c46; *: P; AI: P; AO: P; AV: P | 39 | AO_AV | 6 | Device-Type (nur AO) | R
37 | 21 |  | Low_Limit | Sort: c47; *: P; AI: P; AO: P; AV: P | 40 | AO_AV | 7 | Status_Flags | R
38 | 22 |  | High_Limit | Sort: c48; *: P; AI: P; AO: P; AV: P | 41 | AO_AV | 8 | Event_State | R
39 | 23 |  | Limit_Enable | Sort: c49; *: P; AI: P; AO: P; AV: P | 42 | AO_AV | 9 | Reliability | W1
40 | 24 |  | Deadband | Sort: c50; *: P; AI: P; AO: P; AV: P; LP: U | 43 | AO_AV | 10 | Out_Of_Service | W
41 | 25 |  | Object_Property_Reference | Sort: c51; *: P; EE: P | 44 | AO_AV | 11 | Units | W | b11
42 | 1 | d. Trendauf-zeichnung | Enable | Sort: d11; *: B; TL: B | 45 | AO_AV | 12 | Min_Pres_Value | R | c45
43 | 2 |  | Log_DeviceObjectProperty | Sort: d12; *: B; TL: B | 46 | AO_AV | 13 | Max_Pres_Value | R | c46
44 | 3 |  | Log_Interval | Sort: d13; *: B; TL: B | 47 | AO_AV | 14 | Resolution (nur AO) | R | b41
45 | 4 |  | COV_Resubscription_Interval | Sort: d14; *: B; TL: B | 48 | AO_AV | 15 | Priority_Array | R
46 | 5 |  | Client_COV_Increment | Sort: d15; *: B; TL: B | 49 | AO_AV | 16 | Relinquish_Default | W | b16
47 | 6 |  | Stop_When_Full | Sort: d16; *: B; TL: B | 50 | AO_AV | 17 | COV_Increment | W | b17
48 | 7 |  | Buffer_Size | Sort: d17; *: B; TL: B | 51 | AO_AV | 18 | Time_Delay | W | c43
49 | 8 |  | Logging_Type | Sort: d18; *: B; TL: B | 52 | AO_AV | 19 | Notification_Class | W | c11
50 | 9 |  | Trigger | Sort: d19; *: B; TL: B | 53 | AO_AV | 20 | Low_Limit | W | c47
51 | 10 |  | Notification_Threshold | Sort: d20; *: B; TL: B | 54 | AO_AV | 21 | High_Limit | W | c48
52 | 1 | e. Zeit-management | Date_List | Sort: e11; *: B; CAL: B | 55 | AO_AV | 22 | Deadband | W | c50
53 | 2 |  | Effective_Period | Sort: e12; *: B; SCH: B | 56 | AO_AV | 23 | Limit_Enable | W | c49
54 | 3 |  | Weekly_Schedule | Sort: e13; *: B; SCH: B | 57 | AO_AV | 24 | Event_Enable | W | c12
55 | 4 |  | Exception_Schedule | Sort: e14; *: B; SCH: B | 58 | AO_AV | 25 | Acked_Transitions | R
56 | 5 |  | Schedule_Default | Sort: e15; *: B; SCH: B | 59 | AO_AV | 26 | Notify_Type | W | c13
57 | 6 |  | List_Of_Object_Property_Reference | Sort: e71; *: P; SCH: P | 60 | AO_AV | 27 | Event_Time_Stamps | R
58 | 1 | f. Regler | Setpoint_Reference | Sort: f11; *: B; LP: B | 61 | AO_AV | 28 | Event_Message_Texts | R
59 | 2 |  | Action | Sort: f41; *: P; LP: P | 62 | AO_AV | 29 | Event_Message_Texts_Config | W | c14
60 | 3 |  | Controlled_Variable_ Reference | Sort: f42; *: P; LP: P | 63 | AO_AV | 30 | Event_Detection_Enable | W | c15
61 | 4 |  | Controlled_Variable_Units | Sort: f43; *: P; LP: P | 64 | AO_AV | 31 | Event_Algorithm_Inhibit(_Ref) | R | c42
62 | 5 |  | Minimum_Output | Sort: f44; *: P; LP: P | 65 | AO_AV | 32 | Time_Delay_Normal | W | c44
63 | 6 |  | Maximum_Output | Sort: f45; *: P; LP: P | 66 | AO_AV | 33 | Reliability_Evaluation_Inhibit | R
64 | 7 |  | Manipulated_Variable_ Reference | Sort: f46; *: P; LP: P | 67 | AO_AV | 34 | Property_List | R
65 | 8 |  | Output_Units | Sort: f47; *: P; LP: P | 68 | AO_AV | 35 | Current_Command_Priority | R22
66 | 9 |  | Proportional_Constant | Sort: f71; *: U; LP: U | 69 | BI | 1 | Objekt_Template | ConfCode
67 | 10 |  | Proportional_Constant_Units | Sort: f72; *: U; LP: U | 70 | BI | 2 | Object_Name | R | a11
68 | 11 |  | Derivative_Constant | Sort: f73; *: U; LP: U | 71 | BI | 3 | Description | W | a12
69 | 12 |  | Derivative_Constant_Units | Sort: f74; *: U; LP: U | 72 | BI | 4 | Description Präfix
70 | 13 |  | Integral_Constant | Sort: f75; *: U; LP: U | 73 | BI | 5 | Zweck
71 | 14 |  | Integral_Constant_Units | Sort: f76; *: U; LP: U | 74 | BI | 6 | Device_Type | R
72 | 1 | x. Struktur | Node_Type | Sort: x11; *: B; SV: B | 75 | BI | 7 | Status_Flags | R
73 | 2 |  | Node_Subtype | Sort: x12; *: B; SV: B | 76 | BI | 8 | Event_State | R
74 | 3 |  | Subordinate_List | Sort: x13; *: B; SV: B | 77 | BI | 9 | Reliability | R
75 | 1 | y. Geräte- und Netzwerk-Management | Location | Sort: y11; *: B; DEV: B | 78 | BI | 10 | Out_Of_Service | W
76 | 2 |  | Protocol_Version | Sort: y12; *: B; DEV: B | 79 | BI | 11 | Polarity | W | b12
77 | 3 |  | Protocol_Revision | Sort: y13; *: B; DEV: B | 80 | BI | 12 | Inactive_Text | R | b13
78 | 4 |  | Protocol_Services_Supported | Sort: y14; *: B; DEV: B | 81 | BI | 13 | Active_Text | R | b14
79 | 5 |  | Protocol_Object_Types_Supported | Sort: y15; *: B; DEV: B | 82 | BI | 14 | Change_Of_State_Time | R
80 | 6 |  | UTC_Offset | Sort: y16; *: B; DEV: B | 83 | BI | 15 | Change_Of_State_Count | R0
81 | 7 |  | UTC_Time_Synchronization_Recipients | Sort: y17; *: B; DEV: B | 84 | BI | 16 | Time_Of_State_Count_Reset | W
82 | 8 |  | Time_Synchronization_Recipients | Sort: y18; *: B; DEV: B | 85 | BI | 17 | Elapsed_Active_Time | R0
83 | 9 |  | Time_Synchronization_Interval | Sort: y19; *: B; DEV: B | 86 | BI | 18 | Time_Of_Active_Time_Reset | W
84 | 10 |  | Align_Intervals | Sort: y20; *: B; DEV: B | 87 | BI | 19 | Time_Delay | W | c43
85 | 11 |  | Interval_Offset | Sort: y21; *: B; DEV: B | 88 | BI | 20 | Notification_Class | W | c11
86 | 12 |  | Max_Master | Sort: y22; *: B; DEV: B | 89 | BI | 21 | Alarm_Value | W | c16
87 | 13 |  | Max_Info_Frames | Sort: y23; *: B; DEV: B | 90 | BI | 22 | Event_Enable | W | c12
[24 empty] | 93 | BI | 25 | Event_Time_Stamps | R
|  | * Zuständig: | B = Bauherr/Betreiber (grün) | *: P = Planung (gelb); MO: U = Ausführendes Unternehmen (blau) | Event_Message_Texts_Config | W | c14
[24 empty] | 96 | BI | 28 | Event_Detection_Enable | W | c15
[24 empty] | 97 | BI | 29 | Event_Algorithm_Inhibit(_Ref) | R | c42
[24 empty] | 98 | BI | 30 | Time_Delay_Normal | W | c44
[24 empty] | 99 | BI | 31 | Reliability_Evaluation_Inhibit | R
[24 empty] | 100 | BI | 32 | Property_List | R
[24 empty] | 101 | BO_BV | 1 | Objekt_Template | ConfCode
[24 empty] | 102 | BO_BV | 2 | Object_Name | R | a11
[24 empty] | 103 | BO_BV | 3 | Description | W | a12
[24 empty] | 104 | BO_BV | 4 | Description Präfix
[24 empty] | 105 | BO_BV | 5 | Zweck
[24 empty] | 106 | BO_BV | 6 | Device-Type (nur BO) | R
[24 empty] | 107 | BO_BV | 7 | Status_Flags | R
[24 empty] | 108 | BO_BV | 8 | Event_State | R
[24 empty] | 109 | BO_BV | 9 | Reliability | R
[24 empty] | 110 | BO_BV | 10 | Out_Of_Service | W
[24 empty] | 111 | BO_BV | 11 | Polarity (nur BO) | W | b12
[24 empty] | 112 | BO_BV | 12 | Inactive_Text | W | b13
[24 empty] | 113 | BO_BV | 13 | Active_Text | W | b14
[24 empty] | 114 | BO_BV | 14 | Change_Of_State_Time | R
[24 empty] | 115 | BO_BV | 15 | Change_Of_State_Count | R0
[24 empty] | 116 | BO_BV | 16 | Time_Of_State_Count_Reset | W
[24 empty] | 117 | BO_BV | 17 | Elapsed_Active_Time | R0
[24 empty] | 118 | BO_BV | 18 | Time_Of_Active_Time_Reset | W
[24 empty] | 119 | BO_BV | 19 | Mininum_Off_Time | W | b43
[24 empty] | 120 | BO_BV | 20 | Mininum_On_Time | W | b44
[24 empty] | 121 | BO_BV | 21 | Priority_Array | R
[24 empty] | 122 | BO_BV | 22 | Relinquish_Default | W | b16
[24 empty] | 123 | BO_BV | 23 | Time_Delay | W | c43
[24 empty] | 124 | BO_BV | 24 | Notification_Class | W | c11
[24 empty] | 125 | BO_BV | 25 | Alarm_Value (nur BV) | W | c16
[24 empty] | 126 | BO_BV | 26 | Feedback_Value (nur BO) | W | c19
[24 empty] | 127 | BO_BV | 27 | Event_Enable | W | c12
[24 empty] | 128 | BO_BV | 28 | Acked_Transitions | R
[24 empty] | 129 | BO_BV | 29 | Notify_Type | W | c13
[24 empty] | 130 | BO_BV | 30 | Event_Time_Stamps | R
[24 empty] | 131 | BO_BV | 31 | Event_Message_Texts | R
[24 empty] | 132 | BO_BV | 32 | Event_Message_Texts_Config | W | c14
[24 empty] | 133 | BO_BV | 33 | Event_Detection_Enable | W | c15
[24 empty] | 134 | BO_BV | 34 | Event_Algorithm_Inhibit(_Ref) | R | c42
[24 empty] | 135 | BO_BV | 35 | Time_Delay_Normal | W | c44
[24 empty] | 136 | BO_BV | 36 | Reliability_Evaluation_Inhibit | R
[24 empty] | 137 | BO_BV | 37 | Property_List | R
[24 empty] | 138 | BO_BV | 38 | Current_Command_Priority | R22
[24 empty] | 139 | CAL | 1 | Objekt_Template | ConfCode
[24 empty] | 140 | CAL | 2 | Object_Name | R | a11
[24 empty] | 141 | CAL | 3 | Description | W | a12
[24 empty] | 142 | CAL | 4 | Date_List | W | e11
[24 empty] | 143 | CAL | 5 | Property_List | R
[24 empty] | 144 | DEV | 1 | Objekt_Template | ConfCode
[24 empty] | 145 | DEV | 2 | Object_Name | R | a11
[24 empty] | 146 | DEV | 3 | Location | W | y11
[24 empty] | 147 | DEV | 4 | Description | W | a12
[24 empty] | 148 | DEV | 5 | Description Präfix
[24 empty] | 149 | DEV | 6 | Protocol_Version | R | y12
[24 empty] | 150 | DEV | 7 | Protocol_Revision | R | y13
[24 empty] | 151 | DEV | 8 | Protocol_Services_Supported | R | y14
[24 empty] | 152 | DEV | 9 | Protocol_Object_Types_Supported | R | y15
[24 empty] | 153 | DEV | 10 | Max_Segments_Accepted | R
[24 empty] | 154 | DEV | 11 | Local_Time | W
[24 empty] | 155 | DEV | 12 | Local_Date | W
[24 empty] | 156 | DEV | 13 | UTC_Offset | R | y16
[24 empty] | 157 | DEV | 14 | Daylight_Savings_Status | R
[24 empty] | 158 | DEV | 15 | APDU_Segment_Timeout | W
[24 empty] | 159 | DEV | 16 | APDU_Timeout | W
[24 empty] | 160 | DEV | 17 | Number_Of_APDU_Retries | W
[24 empty] | 161 | DEV | 18 | Time_Synchronization_Recipients | W | y18
[24 empty] | 162 | DEV | 19 | Max_Master | W | y22
[24 empty] | 163 | DEV | 20 | Max_Info_Frames | W | y23
[24 empty] | 164 | DEV | 21 | Configuration_Files | R
[24 empty] | 165 | DEV | 22 | Last_Restore_Time | R
[24 empty] | 166 | DEV | 23 | Backup_Failure_Timeout | R
[24 empty] | 167 | DEV | 24 | Backup_Preparation_Time | R
[24 empty] | 168 | DEV | 25 | Restore_Preparation_Time | R
[24 empty] | 169 | DEV | 26 | Restore_Completion_Time | R
[24 empty] | 170 | DEV | 27 | Backup_And_Restore_State | R
[24 empty] | 171 | DEV | 28 | Active_COV_Subscriptions | R
[24 empty] | 172 | DEV | 29 | Last_Restart_Reason | R
[24 empty] | 173 | DEV | 30 | Time_Of_Device_Restart | R
[24 empty] | 174 | DEV | 31 | Restart_Notification_Recipients | R
[24 empty] | 175 | DEV | 32 | UTC_Time_Synchronization_Recipients | W | y17
[24 empty] | 176 | DEV | 33 | Time_Synchronization_Interval | W | y19
[24 empty] | 177 | DEV | 34 | Align_Intervals | R | y20
[24 empty] | 178 | DEV | 35 | Interval_Offset | R | y21
[24 empty] | 179 | DEV | 36 | Serial_Number | R
[24 empty] | 180 | DEV | 37 | Property_List | R
[24 empty] | 181 | EE | 1 | Objekt_Template | ConfCode
[24 empty] | 182 | EE | 2 | Object_Name | R | a11
[24 empty] | 183 | EE | 3 | Description | W | a12
[24 empty] | 184 | EE | 4 | Description Präfix
[24 empty] | 185 | EE | 5 | Event_Type | W | c23
[24 empty] | 186 | EE | 6 | Notify_Type | W | c13
[24 empty] | 187 | EE | 7 | Event_Parameters | W | c24
[24 empty] | 188 | EE | 8 | Object_Property_Reference | W | c51
[24 empty] | 189 | EE | 9 | Event_State | R
[24 empty] | 190 | EE | 10 | Event_Enable | W | c12
[24 empty] | 191 | EE | 11 | Acked_Transitions | R
[24 empty] | 192 | EE | 12 | Notification_Class | W | c11
[24 empty] | 193 | EE | 13 | Event_Time_Stamps | R
[24 empty] | 194 | EE | 14 | Event_Message_Texts | R
[24 empty] | 195 | EE | 15 | Event_Message_Texts_Config | W | c14
[24 empty] | 196 | EE | 16 | Event_Detection_Enable | W | c15
[24 empty] | 197 | EE | 17 | Event_Algorithm_Inhibit(_Ref) | R | c42
[24 empty] | 198 | EE | 18 | Time_Delay_Normal | W | c44
[24 empty] | 199 | EE | 19 | Status_Flags | R
[24 empty] | 200 | EE | 20 | Reliability | W1
[24 empty] | 201 | EE | 21 | Reliability_Evaluation_Inhibit | R
[24 empty] | 202 | EE | 22 | Property_List | R
[24 empty] | 203 | LP | 1 | Objekt_Template | ConfCode
[24 empty] | 204 | LP | 2 | Object_Name | R | a11
[24 empty] | 205 | LP | 3 | Present_Value | W1
[24 empty] | 206 | LP | 4 | Description | W | a12
[24 empty] | 207 | LP | 5 | Description Präfix
[24 empty] | 208 | LP | 6 | Status_Flags | R
[24 empty] | 209 | LP | 7 | Event_State | R
[24 empty] | 210 | LP | 8 | Reliability | R
[24 empty] | 211 | LP | 9 | Out_Of_Service | W
[24 empty] | 212 | LP | 10 | Update_Interval | R
[24 empty] | 213 | LP | 11 | Output_Units | R | f47
[24 empty] | 214 | LP | 12 | Manipulated_Variable_Reference | R | f46
[24 empty] | 215 | LP | 13 | Controlled_Variable_Reference | R | f42
[24 empty] | 216 | LP | 14 | Controlled_Variable_Value | R
[24 empty] | 217 | LP | 15 | Controlled_Variable_Units | R | f43
[24 empty] | 218 | LP | 16 | Setpoint_Reference | R | f11
[24 empty] | 219 | LP | 17 | Setpoint | R
[24 empty] | 220 | LP | 18 | Action | W | f41
[24 empty] | 221 | LP | 19 | Proportional_Constant | W | f71
[24 empty] | 222 | LP | 20 | Proportional_Constant_Units | R | f72
[24 empty] | 223 | LP | 21 | Integral_Constant | W | f75
[24 empty] | 224 | LP | 22 | Integral_Constant_Units | R | f76
[24 empty] | 225 | LP | 23 | Derivative_Constant | W | f73
[24 empty] | 226 | LP | 24 | Derivative_Constant_Units | R | f74
[24 empty] | 227 | LP | 25 | Bias | W
[24 empty] | 228 | LP | 26 | Maximum_Output | W | f45
[24 empty] | 229 | LP | 27 | Minimum_Output | W | f44
[24 empty] | 230 | LP | 28 | Priority_For_Writing | R | b18
[24 empty] | 231 | LP | 29 | COV_Increment | W | b17
[24 empty] | 232 | LP | 30 | Time_Delay | W | c43
[24 empty] | 233 | LP | 31 | Notification_Class | W | c11
[24 empty] | 234 | LP | 32 | Time_Delay_Normal | W | c44
[24 empty] | 235 | LP | 33 | Error_Limit | W
[24 empty] | 236 | LP | 34 | Deadband | W | c50
[24 empty] | 237 | LP | 35 | Low_Diff_Limit | W
[24 empty] | 238 | LP | 36 | Acked_Transitions | R
[24 empty] | 239 | LP | 37 | Notify_Type | W | c13
[24 empty] | 240 | LP | 38 | Event_Time_Stamps | R
[24 empty] | 241 | LP | 39 | Event_Message_Texts | R
[24 empty] | 242 | LP | 40 | Event_Message_Texts_Config | W | c14
[24 empty] | 243 | LP | 41 | Event_Detection_Enable | W | c15
[24 empty] | 244 | LP | 42 | Event_Algorithm_Inhibit(_Ref) | R | c42
[24 empty] | 245 | LP | 43 | Reliability_Evaluation_Inhibit | R
[24 empty] | 246 | LP | 44 | Property_List | R
[24 empty] | 247 | MI | 1 | Objekt_Template | ConfCode
[24 empty] | 248 | MI | 2 | Object_Name | R | a11
[24 empty] | 249 | MI | 3 | Description | W | a12
[24 empty] | 250 | MI | 4 | Description Präfix
[24 empty] | 251 | MI | 5 | Device_Type | R
[24 empty] | 252 | MI | 6 | Status_Flags | R
[24 empty] | 253 | MI | 7 | Event_State | R
[24 empty] | 254 | MI | 8 | Reliability | W1
[24 empty] | 255 | MI | 9 | Out_Of_Service | W
[24 empty] | 256 | MI | 10 | Number_Of_States | R | b42
[24 empty] | 257 | MI | 11 | State_Text | W | b15
[24 empty] | 258 | MI | 12 | Time_Delay | W | c43
[24 empty] | 259 | MI | 13 | Notification_Class | W | c11
[24 empty] | 260 | MI | 14 | Alarm_Values | W | c17
[24 empty] | 261 | MI | 15 | Fault_Values | W | c18
[24 empty] | 262 | MI | 16 | Event_Enable | W | c12
[24 empty] | 263 | MI | 17 | Acked_Transitions | R
[24 empty] | 264 | MI | 18 | Notify_Type | W | c13
[24 empty] | 265 | MI | 19 | Event_Time_Stamps | R
[24 empty] | 266 | MI | 20 | Event_Message_Texts | R
[24 empty] | 267 | MI | 21 | Event_Message_Texts_Config | W | c14
[24 empty] | 268 | MI | 22 | Event_Detection_Enable | W | c15
[24 empty] | 269 | MI | 23 | Event_Algorithm_Inhibit(_Ref) | R | c42
[24 empty] | 270 | MI | 24 | Time_Delay_Normal | W | c44
[24 empty] | 271 | MI | 25 | Reliability_Evaluation_Inhibit | R
[24 empty] | 272 | MI | 26 | Property_List | R
[24 empty] | 273 | MO_MV | 1 | Objekt_Template | ConfCode
[24 empty] | 274 | MO_MV | 2 | Object_Name | R | a11
[24 empty] | 275 | MO_MV | 3 | Description | W | a12
[24 empty] | 276 | MO_MV | 4 | Description Präfix
[24 empty] | 277 | MO_MV | 5 | Device_Type (nur MO) | R
[24 empty] | 278 | MO_MV | 6 | Status_Flags | R
[24 empty] | 279 | MO_MV | 7 | Event_State | R
[24 empty] | 280 | MO_MV | 8 | Reliability | W1
[24 empty] | 281 | MO_MV | 9 | Out_Of_Service | W
[24 empty] | 282 | MO_MV | 10 | Number_Of_States | R | b42
[24 empty] | 283 | MO_MV | 11 | State_Text | W | b15
[24 empty] | 284 | MO_MV | 12 | Priority_Array | R
[24 empty] | 285 | MO_MV | 13 | Relinquish_Default | W | b16
[24 empty] | 286 | MO_MV | 14 | Time_Delay | W | c43
[24 empty] | 287 | MO_MV | 15 | Feedback_Value (nur MO) | R | c19
[24 empty] | 288 | MO_MV | 16 | Notification_Class | W | c11
[24 empty] | 289 | MO_MV | 17 | Alarm_Values (nur MV) | W | c17
[24 empty] | 290 | MO_MV | 18 | Fault_Values (nur MV) | W | c18
[24 empty] | 291 | MO_MV | 19 | Event_Enable | W | c12
[24 empty] | 292 | MO_MV | 20 | Acked_Transitions | R
[24 empty] | 293 | MO_MV | 21 | Notify_Type | W | c13
[24 empty] | 294 | MO_MV | 22 | Event_Time_Stamps | R
[24 empty] | 295 | MO_MV | 23 | Event_Message_Texts | R
[24 empty] | 296 | MO_MV | 24 | Event_Message_Texts_Config | W | c14
[24 empty] | 297 | MO_MV | 25 | Event_Detection_Enable | W | c15
[24 empty] | 298 | MO_MV | 26 | Event_Algorithm_Inhibit(_Ref) | R | c42
[24 empty] | 299 | MO_MV | 27 | Time_Delay_Normal | W | c44
[24 empty] | 300 | MO_MV | 28 | Reliability_Evaluation_Inhibit | R
[24 empty] | 301 | MO_MV | 29 | Property_List | R
[24 empty] | 302 | MO_MV | 30 | Current_Command_Priority | R22
[24 empty] | 303 | NC | 1 | Objekt_Template | ConfCode
[24 empty] | 304 | NC | 2 | Object_Name | R | a11
[24 empty] | 305 | NC | 3 | Object_Identifier | R | a71
[24 empty] | 306 | NC | 4 | Description | W | a12
[24 empty] | 307 | NC | 5 | Description Präfix
[24 empty] | 308 | NC | 6 | Priority | W | c20
[24 empty] | 309 | NC | 7 | Ack_Required | W | c21
[24 empty] | 310 | NC | 8 | Recipient_List | W | c22
[24 empty] | 311 | NC | 9 | Property_List | R
[24 empty] | 312 | SCH | 1 | Objekt_Template | ConfCode
[24 empty] | 313 | SCH | 2 | Object_Name | R | a11
[24 empty] | 314 | SCH | 3 | Description | W | a12
[24 empty] | 315 | SCH | 4 | Description Präfix
[24 empty] | 316 | SCH | 5 | Effective_Period | W | e12
[24 empty] | 317 | SCH | 6 | Weekly_Schedule | W | e13
[24 empty] | 318 | SCH | 7 | Exception_Schedule | W | e14
[24 empty] | 319 | SCH | 8 | Schedule_Default | W | e15
[24 empty] | 320 | SCH | 9 | List_Of_Object_ Property_References | W | e71
[24 empty] | 321 | SCH | 10 | Priority_For_Writing | W | b18
[24 empty] | 322 | SCH | 11 | Status_Flags | R
[24 empty] | 323 | SCH | 12 | Reliability | R
[24 empty] | 324 | SCH | 13 | Out_Of_Service | W
[24 empty] | 325 | SCH | 14 | Notification_Class | W | c11
[24 empty] | 326 | SCH | 15 | Event_Enable | W | c12
[24 empty] | 327 | SCH | 16 | Event_State | W
[24 empty] | 328 | SCH | 17 | Acked_Transitions | R
[24 empty] | 329 | SCH | 18 | Notify_Type | W | c13
[24 empty] | 330 | SCH | 19 | Event_Time_Stamps | R
[24 empty] | 331 | SCH | 20 | Event_Message_Texts | R
[24 empty] | 332 | SCH | 21 | Event_Message_Texts_Config | W | c14
[24 empty] | 333 | SCH | 22 | Event_Detection_Enable | W | c15
[24 empty] | 334 | SCH | 23 | Reliability_Evaluation_Inhibit | RX¦O
[24 empty] | 335 | SCH | 24 | Property_List | R
[24 empty] | 336 | SV | 1 | Objekt_Template | ConfCode
[24 empty] | 337 | SV | 6 | Object_Name | R | a11
[24 empty] | 338 | SV | 7 | Description | O | a12
[24 empty] | 339 | SV | 2 | Node_Type | R | x11
[24 empty] | 340 | SV | 3 | Node_Subtype | R | x12
[24 empty] | 341 | SV | 4 | Subordinate_List | R | x13
[24 empty] | 342 | SV | 5 | Property_List | R
[24 empty] | 343 | TL | 1 | Objekt_Template | ConfCode
[24 empty] | 344 | TL | 2 | Object_Name | R | a11
[24 empty] | 345 | TL | 3 | Description | W | a12
[24 empty] | 346 | TL | 4 | Enable | W | d11
[24 empty] | 347 | TL | 5 | Start_Time | W
[24 empty] | 348 | TL | 6 | Stop_Time | R
[24 empty] | 349 | TL | 7 | Log_DeviceObjectProperty | W | d12
[24 empty] | 350 | TL | 8 | Log_Interval | W | d13
[24 empty] | 351 | TL | 9 | COV_Resubscription_Interval | R | d14
[24 empty] | 352 | TL | 10 | Client_COV_Increment | W | d15
[24 empty] | 353 | TL | 11 | Stop_When_Full | W | d16
[24 empty] | 354 | TL | 12 | Buffer_Size | W | d17
[24 empty] | 355 | TL | 13 | Record_Count | W
[24 empty] | 356 | TL | 14 | Total_Record_Count | R
[24 empty] | 357 | TL | 15 | Logging_Type | W | d18
[24 empty] | 358 | TL | 16 | Trigger | W | d19
[24 empty] | 359 | TL | 17 | Status_Flags | R
[24 empty] | 360 | TL | 18 | Reliability | W1
[24 empty] | 361 | TL | 19 | Records_Since_Notification | R
[24 empty] | 362 | TL | 20 | Notification_Threshold | W | d20
[24 empty] | 363 | TL | 21 | Last_Notify_Record | R
[24 empty] | 364 | TL | 22 | Event_State | R
[24 empty] | 365 | TL | 23 | Notification_Class | W | c11
[24 empty] | 366 | TL | 24 | Event_Enable | W | c12
[24 empty] | 367 | TL | 25 | Acked_Transitions | R
[24 empty] | 368 | TL | 26 | Notify_Type | W | c13
[24 empty] | 369 | TL | 27 | Event_Time_Stamps | R
[24 empty] | 370 | TL | 28 | Event_Message_Texts | R
[24 empty] | 371 | TL | 29 | Event_Message_Texts_Config | W | c14
[24 empty] | 372 | TL | 30 | Event_Detection_Enable | W | c15
[24 empty] | 373 | TL | 31 | Property_List | R

## 23 MinCharStringLength
Lfd. Nr. | Property | AMEV-Profil
|  | MBE | AS-C und AS-D
| 1 | 2 | 3
1 | Object_Name | 64 | 64
2 | Description | 255 | 255
3 | Profile_Name | 64 | keine Vorgabe
4 | Device_Type | 64 | 64
5 | Inactive_Text | 32 | 32
6 | Active_Text | 32 | 32
7 | State_Text | 32 (je Zustand) | 32 (je Zustand)
8 | Event_Message_Texts | 255 | 255
9 | Event_Message_Texts_Conf | 255 | 255
10 | Location | 64 | 64
11 | Vendor_Name | 64 | keine Vorgabe
12 | Model_Name | 64 | keine Vorgabe
13 | Application_Software_Version | 64 | keine Vorgabe

## 24 Priority_Array
Priority _Array | Verwendung (DIN EN ISO 16484-5 Tab. 19-1) | Empfehlung | Beschreibung / Beispiel
1 | Manual Life Safety | Manual Life Safety | z. B. Schlüsselsteuerung durch Feuerwehr
2 | Automatic Life Safety | Automatic Life Safety | z. B. Brandschaltung/Übersteuerung durch eine Brandnotsteuerung
3 | Available |  | (Reserve)
4 | Available |  | (Reserve)
5 | Critical Aggregate Control | Critical Aggregate Control | Übersteuerung der minimalen Ein-/Aus­schaltzeiten, wenn ein verhinderter Gesamtschaden größer wäre als ein ev. Geräteschaden, z. B. Lastabwurf
6 | Minimum On/Off | Minimum On/Off | Mindest-Ein-/Ausschaltzeiten von Objekten, z. B. Verdichter Kältemaschine
7 | Available |  | (Reserve)
8 | Manual Operator | Übersteuerung durch MBE, BAE, ASE oder HMI | Handschaltung über MBE, BAE, ASE oder HMI durch einen Benutzer
9 | Available |  | (Reserve)
10 | Available | Übergeordneter Automatikbetrieb | Übersteuerung durch Zentralfunktion, z. B. Putzbeleuchtung
11 | Available |  | (Reserve)
12 | Available | Zeitschaltung | Das zu steuernde Objekt wird vom Objekt Schedule beschrieben
13 | Available |  | (Reserve)
14 | Available |  | (Reserve)
15 | Available | Automatikbetrieb | Funktionen der Ansteuerung des Automatikbetriebes (Programm)
16 | Available |  | (Reserve; bisher: Automatikbetrieb)
- | Relinquish_Default | Relinquish_Default | Wird bei Projektierung im Objekt eingestellt

## 25 Meldeklasse
Lfd. Nr. | Object_ Identifier | Meldeklasse Bezeichnung | Priority | Ack_Required
1 | NC100 | Meldeklasse Gefahr Personen | {10,11,110} | {true,true,true}
2 | NC150 | Meldeklasse Gefahr Liegenschaft | {15,16,115} | {true,true,true}
3 | NC200 | Meldeklasse Alarm | {20,21,120} | {true,true,false}
4 | NC250 | Meldeklasse Voralarm | {25,26,125} | {true,true,false}
5 | NC300 | Meldeklasse Störung | {30,31,130} | {true,true,false}
6 | NC350 | Meldeklasse Anormal | {35,36,135} | {false,false,false}
7 | NC400 | Meldeklasse Wartung | {40,41,140} | {false,false,false}
8 | NC425 | Meldeklasse Wartung (quittierbar) | {42,43,142} | {true,false,false}
9 | NC450 | Meldeklasse Revision | {45,46,145} | {false,false,false}
10 | NC500 | Meldeklasse Handeingriff | {50,51,150} | {false,false,false}
11 | NC600 | Meldeklasse System | {60,61,160} | {true,false,false}
12 | NC700 | Meldeklasse Trend | {70,71,170} | {false,false,false}
13 | NC800 | Meldeklasse Sonstiges | {80,81,180} | {false,false,false}

## 26 EventParameter
Objekt_Template | Event_Type / Event_Algorithm | Event_Parameters | Anwendungsbeispiel
EE_COB | CHANGE_OF_BITSTRING | Time_Delay | Überwachung von Handstellung am Modul (Overridden) und Handstellungen über Bedieneinheit (Out_Of_Service)
Bitmask
List_Of_Bitstring_Values
EE_COS oder | CHANGE_OF_STATE | Time_Delay | Überwachung von Zuständen binärer oder mehrstufiger Werte (oder Current_Command_Priortiy ab Rev.22)
EE_CCP |  | List_Of_Values
EE_COV | CHANGE_OF_VALUE | Time_Delay | Überwachung von Sollwertänderungen
Bitmask
Referenced_Property_Increment
EE_CMDF oder | COMMAND_FAILURE | Time_Delay | Überwachung von Ausführkontrollen
EE_GM_PSA |  | Feedback_Property_Reference
EE_FLIM | FLOATING_LIMIT | Time_Delay | Überwachung von Abweichungen
Setpoint_Reference
Low_Diff_Limit
High_Diff_Limit
Deadband
EE_OOR | OUT_OF_RANGE | Time_Delay | Überwachung von Grenzwerten
Low_Limit
High_Limit
Deadband
| BUFFER_READY | Notification_Threshold
Previous_Notification_Count